## buses
Row 3 contains the names of relevant pypsa variables
Bus Name | Nominal Voltage (kV)
name | v_nom

## lines
Row 3 contains the names of relevant pypsa variables
Line Name | Start Bus | End Bus | Length(km) | Conductor | Line Resistance (Ohm) | Line Inductive Reactance (Ohm) | Line Shunt Susceptance (Siemens) | Line Nominal Capacity (MVA)
name | bus0 | bus1 |  |  | r | x | b | s_nom
BheramaraHVDC1_400kV_DCtoBangladesh Border1_400kV_DC_Line1 | BheramaraHVDC1_400kV_DC | BangladeshBorder1_400kV_DC | 27.35 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
BheramaraHVDC1_400kV_DCtoBangladesh Border1_400kV_DC_Line2 | BheramaraHVDC1_400kV_DC | BangladeshBorder1_400kV_DC | 27.35 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
Aminbazar_400kVtoMeghnaghat_400kV_Line1 | Aminbazar_400kV | Meghnaghat_400kV | 55 | Quad Egret | 0.02755 | 0.081959 | 2.6525e-05 | 400
Aminbazar_400kVtoMeghnaghat_400kV_Line2 | Aminbazar_400kV | Meghnaghat_400kV | 55 | Quad Egret | 0.02755 | 0.081959 | 2.6525e-05 | 400
SuryamaninagarRecvBus_132kVtoCumillaSouth_132kV_Line1 | SuryamaninagarRecvBus_132kV | CumillaSouth_132kV | 47 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
SuryamaninagarRecvBus_132kVtoCumillaSouth_132kV_Line2 | SuryamaninagarRecvBus_132kV | CumillaSouth_132kV | 47 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
Bibiyana_400kVtoKaliakoir_400kV_Line1 | Bibiyana_400kV | Kaliakoir_400kV | 169.5 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
Bibiyana_400kVtoKaliakoir_400kV_Line2 | Bibiyana_400kV | Kaliakoir_400kV | 169.5 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
AshuganjNorth_400kVtoBhulta_400kV_Line1 | AshuganjNorth_400kV | Bhulta_400kV | 69 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
AshuganjNorth_400kVtoBhulta_400kV_Line2 | AshuganjNorth_400kV | Bhulta_400kV | 69 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
Payra_400kVtoGopalganjNorth_400kV_Line1 | Payra_400kV | GopalganjNorth_400kV | 163.55 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
Payra_400kVtoGopalganjNorth_400kV_Line2 | Payra_400kV | GopalganjNorth_400kV | 163.55 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
BSRM_230kVtoMirsarai_230kV_Line1 | BSRM_230kV | Mirsarai_230kV | 16.5 | Twin Finch | 0.027187 | 0.12927 | 1.4337e-05 | 400
BSRM_230kVtoMirsarai_230kV_Line2 | BSRM_230kV | Mirsarai_230kV | 16.5 | Twin Finch | 0.027187 | 0.12927 | 1.4337e-05 | 400
BheramaraHVDC2_400kV_DCtoBangladeshBorder2_400kV_DC_Line1 | BheramaraHVDC2_400kV_DC | BangladeshBorder2_400kV_DC | 28 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
BheramaraHVDC2_400kV_DCtoBangladeshBorder2_400kV_DC_Line2 | BheramaraHVDC2_400kV_DC | BangladeshBorder2_400kV_DC | 28 | Twin Finch | 0.031985 | 0.12927 | 1.4337e-05 | 400
PayraPP_400kVtoPayra_400kV_Line1 | PayraPP_400kV | Payra_400kV | 1.2 | Quad Finch | 0.06397 | 0.2362 | 7.1685e-06 | 400
PayraPP_400kVtoPayra_400kV_Line2 | PayraPP_400kV | Payra_400kV | 1.2 | Quad Finch | 0.06397 | 0.2362 | 7.1685e-06 | 400
Banskhali_400kVtoMadunaghatNew_400kV_Line1 | Banskhali_400kV | MadunaghatNew_400kV | 55.5 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
Banskhali_400kVtoMadunaghatNew_400kV_Line2 | Banskhali_400kV | MadunaghatNew_400kV | 55.5 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
AdaniPPRecvBus_400kVtoRahanpur_400kV_Line1 | AdaniPPRecvBus_400kV | Rahanpur_400kV | 134 | Twin Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
AdaniPPRecvBus_400kVtoRahanpur_400kV_Line2 | AdaniPPRecvBus_400kV | Rahanpur_400kV | 134 | Twin Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
Rampal_400kVtoGopalganjNorth_400kV_Line1 | Rampal_400kV | GopalganjNorth_400kV | 96.7 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
Rampal_400kVtoGopalganjNorth_400kV_Line2 | Rampal_400kV | GopalganjNorth_400kV | 96.7 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
GopalganjNorth_400kVtoAminbazar_400kV_Line1 | GopalganjNorth_400kV | Aminbazar_400kV | 75.3 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
GopalganjNorth_400kVtoAminbazar_400kV_Line2 | GopalganjNorth_400kV | Aminbazar_400kV | 75.3 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
BoguraWest_400kVtoRahanpur_400kV_Line1 | BoguraWest_400kV | Rahanpur_400kV | 105 | Twin Finch | 0.027187 | 0.12927 | 1.4337e-05 | 400
BoguraWest_400kVtoRahanpur_400kV_Line2 | BoguraWest_400kV | Rahanpur_400kV | 105 | Twin Finch | 0.027187 | 0.12927 | 1.4337e-05 | 400
Barishal307MWPP_400kVtoPayraPP_400kV_Line1 | Barishal307MWPP_400kV | PayraPP_400kV | 27.8 | Quad Finch | 0.06397 | 0.2362 | 7.1685e-06 | 400
Barishal307MWPP_400kVtoPayraPP_400kV_Line2 | Barishal307MWPP_400kV | PayraPP_400kV | 27.8 | Quad Finch | 0.06397 | 0.2362 | 7.1685e-06 | 400
Matarbari_400kVtoBanskhali_400kV_Line1 | Matarbari_400kV | Banskhali_400kV | 38 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
Matarbari_4002kVtoBanskhali_400kV_Line2 | Matarbari_400kV | Banskhali_400kV | 38 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
MadunaghatNew_400kVtoKorerhat_400kV_Line1 | MadunaghatNew_400kV | Korerhat_400kV | 66 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
MadunaghatNew_400kVtoKorerhat_400kV_Line2 | MadunaghatNew_400kV | Korerhat_400kV | 66 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
Meghnaghat_400kVtoKorerhat_400kV_Line1 | Meghnaghat_400kV | Korerhat_400kV | 151 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
Meghnaghat_400kVtoKorerhat_400kV_Line2 | Meghnaghat_400kV | Korerhat_400kV | 151 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
RNPP_400kVtoBoguraWest_400kV_Line1 | RNPP_400kV | BoguraWest_400kV | 90 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
BoguraWest_400kVtoBarapukuriaNorth_400kV_Line1 | BoguraWest_400kV | BarapukuriaNorth_400kV | 112 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
BoguraWest_400kVtoBarapukuriaNorth_400kV_Line2 | BoguraWest_400kV | BarapukuriaNorth_400kV | 112 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
PayraPP_400kVtoAmtali_400kV_Line1 | PayraPP_400kV | Amtali_400kV | 17 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
PayraPP_400kVtoAmtali_400kV_Line2 | PayraPP_400kV | Amtali_400kV | 17 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
GopalganjNorth_400kVtoAmtali_400kV_Line1 | GopalganjNorth_400kV | Amtali_400kV | 147 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
GopalganjNorth_400kVtoAmtali_400kV_Line2 | GopalganjNorth_400kV | Amtali_400kV | 147 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
Amtali_400kVtoRNPL_400kV_Line1 | Amtali_400kV | RNPL_400kV | 9.9 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
Amtali_400kVtoRNPL_400kV_Line2 | Amtali_400kV | RNPL_400kV | 9.9 | Quad Finch | 0.015992 | 0.075809 | 2.8674e-05 | 400
Bogura_400kVtoKaliakoir_400kV_Line1 | Bogura_400kV | Kaliakoir_400kV | 73 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
Bogura_400kVtoKaliakoir_400kV_Line2 | Bogura_400kV | Kaliakoir_400kV | 73 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
Aminbazar_400kVtoKaliakoir_400kV_Line1 | Aminbazar_400kV | Kaliakoir_400kV | 51 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
RNPP_400kVtoGopalganjNorth_400kV_Line1 | RNPP_400kV | GopalganjNorth_400kV | 156 | Quad Finch | 0.013593 | 0.075809 | 2.8674e-05 | 400
Ghorashal_230kVtoIshwardi_230kV_Line1 | Ghorashal_230kV | Ishwardi_230kV | 175 | Mallard | 0.08831 | 0.2441 | 6.8729e-06 | 230
Ghorashal_230kVtoIshwardi_230kV_Line2 | Ghorashal_230kV | Ishwardi_230kV | 175 | Mallard | 0.08831 | 0.2441 | 6.8729e-06 | 230
Tongi_230kVtoGhorashal_230kV_Line1 | Tongi_230kV | Ghorashal_230kV | 27 | Mallard | 0.070648 | 0.2441 | 6.8729e-06 | 230
Tongi_230kVtoGhorashal_230kV_Line2 | Tongi_230kV | Ghorashal_230kV | 27 | Mallard | 0.070648 | 0.2441 | 6.8729e-06 | 230
Ghorashal_230kVtoAshuganj_230kV_Line1 | Ghorashal_230kV | Ashuganj_230kV | 44 | Mallard | 0.08831 | 0.2441 | 6.8729e-06 | 230
Ghorashal_230kVtoAshuganj_230kV_Line2 | Ghorashal_230kV | Ashuganj_230kV | 44 | Mallard | 0.08831 | 0.2441 | 6.8729e-06 | 230
Raozan_230kVtoHathazari_230kV_Line1 | Raozan_230kV | Hathazari_230kV | 22.5 | Twin 300 sqmm | 0.1101 | 0.2559 | 6.5703e-06 | 230
Raozan_230kVtoHathazari_230kV_Line2 | Raozan_230kV | Hathazari_230kV | 22.5 | Twin 300 sqmm | 0.1101 | 0.2559 | 6.5703e-06 | 230
Ashuganj_230kVtoCumillaNorth_230kV_Line1 | Ashuganj_230kV | CumillaNorth_230kV | 79 | Finch | 0.06397 | 0.2362 | 7.1685e-06 | 230
Ashuganj_230kVtoCumillaNorth_230kV_Line2 | Ashuganj_230kV | CumillaNorth_230kV | 79 | Finch | 0.06397 | 0.2362 | 7.1685e-06 | 230
Ghorashal_230kVtoBhulta_230kV_Line1 | Ghorashal_230kV | Bhulta_230kV | 50 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Ghorashal_230kVtoBhulta_230kV_Line2 | Ghorashal_230kV | Bhulta_230kV | 50 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Bhulta_230kVtoRampura_230kV_Line1 | Bhulta_230kV | Rampura_230kV | 20 | Twin Mallard
Bhulta_230kVtoRampura_230kV_Line2 | Bhulta_230kV | Rampura_230kV | 20 | Twin Mallard
Haripur_230kVtoBhulta_230kV_Line1 | Haripur_230kV | Bhulta_230kV | 22 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Haripur_230kVtoBhulta_230kV_Line2 | Haripur_230kV | Bhulta_230kV | 22 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Bhulta_230kVtoRampura_230kV_Line3 | Bhulta_230kV | Rampura_230kV | 20 | Twin Mallard
Bhulta_230kVtoRampura_230kV_Line4 | Bhulta_230kV | Rampura_230kV | 20 | Twin Mallard
Haripur_230kVtoMeghnaghat_230kV_Line1 | Haripur_230kV | Meghnaghat_230kV | 12.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Haripur_230kVtoMeghnaghat_230kV_Line2 | Haripur_230kV | Meghnaghat_230kV | 12.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Meghnaghat_230kVtoShyampur_230kV_Line1 | Meghnaghat_230kV | Shyampur_230kV | 12.25 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Meghnaghat_230kVtoShyampur_230kV_Line2 | Meghnaghat_230kV | Shyampur_230kV | 12.25 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Shyampur_230kVtoHasnabad_230kV_Line1 | Shyampur_230kV | Hasnabad_230kV | 12.25 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Shyampur_230kVtoHasnabad_230kV_Line2 | Shyampur_230kV | Hasnabad_230kV | 12.25 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
CumillaNorth_230kVtoFeniNorth_230kV_Line1 | CumillaNorth_230kV | FeniNorth_230kV | 70 | Finch | 0.06397 | 0.2362 | 7.1685e-06 | 230
CumillaNorth_230kVtoFeniNorth_230kV_Line2 | CumillaNorth_230kV | FeniNorth_230kV | 70 | Finch | 0.06397 | 0.2362 | 7.1685e-06 | 230
FeniNorth_230kVtoBSRM_230kV_Line1 | FeniNorth_230kV | BSRM_230kV | 26 | Finch
FeniNorth_230kVtoBSRM_230kV_Line2 | FeniNorth_230kV | BSRM_230kV | 26 | Finch
BSRM_230kVtoGPH_230kV_Line1 | BSRM_230kV | GPH_230kV | 40 | Finch
BSRM_230kVtoGPH_230kV_Line2 | BSRM_230kV | GPH_230kV | 40 | Finch
GPH_230kVtoAKSPL_230kV_Line1 | GPH_230kV | AKSPL_230kV | 13 | Finch
GPH_230kVtoAKSPL_230kV_Line2 | GPH_230kV | AKSPL_230kV | 13 | Finch
AKSPL_230kVtoHathazari_230kV_Line1 | AKSPL_230kV | Hathazari_230kV | 9 | Finch
AKSPL_230kVtoHathazari_230kV_Line2 | AKSPL_230kV | Hathazari_230kV | 9 | Finch
AESHaripur_230kVtoHaripur_230kV_Line1 | AESHaripur_230kV | Haripur_230kV | 2.4 | Finch | 0.06397 | 0.2362 | 7.1685e-06 | 230
AESHaripur_230kVtoHaripur_230kV_Line2 | AESHaripur_230kV | Haripur_230kV | 2.4 | Finch | 0.06397 | 0.2362 | 7.1685e-06 | 230
CumillaNorth_230kVtoMeghnaghat_230kV_Line1 | CumillaNorth_230kV | Meghnaghat_230kV | 58 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
CumillaNorth_230kVtoMeghnaghat_230kV_Line2 | CumillaNorth_230kV | Meghnaghat_230kV | 58 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Tongi_230kVtoKaliakoir_230kV_Line1 | Tongi_230kV | Kaliakoir_230kV | 25.2 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Tongi_230kVtoKaliakoir_230kV_Line2 | Tongi_230kV | Kaliakoir_230kV | 25.2 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Kaliakoir_230kVtoAminbazar_230kV_Line1 | Kaliakoir_230kV | Aminbazar_230kV | 32 | Twin AAAC
Kaliakoir_230kVtoAminbazar_230kV_Line2 | Kaliakoir_230kV | Aminbazar_230kV | 32 | Twin AAAC
Aminbazar_230kVtoKeraniganj_230kV_Line1 | Aminbazar_230kV | Keraniganj_230kV | 10.75 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Aminbazar_230kVtoKeraniganj_230kV_Line2 | Aminbazar_230kV | Keraniganj_230kV | 10.75 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Hasnabad_230kVtoKeraniganj_230kV_Line1 | Hasnabad_230kV | Keraniganj_230kV | 10.75 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Hasnabad_230kVtoKeraniganj_230kV_Line2 | Hasnabad_230kV | Keraniganj_230kV | 10.75 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Ashuganj_230kVtoSripur_230kV_Line1 | Ashuganj_230kV | Sripur_230kV | 75 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Ashuganj_230kVtoSripur_230kV_Line2 | Ashuganj_230kV | Sripur_230kV | 75 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Sripur_230kVtoSirajganjSouthWest_230kV_Line1 | Sripur_230kV | SirajganjSouthWest_230kV | 69 | Twin AAAC
Sripur_230kVtoSirajganjSouthWest_230kV_Line2 | Sripur_230kV | SirajganjSouthWest_230kV | 69 | Twin AAAC
KhulnaSouth_230kVtoJhenaidahSouth_230kV_Line1 | KhulnaSouth_230kV | JhenaidahSouth_230kV | 96 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
KhulnaSouth_230kVtoJhenaidahSouth_230kV_Line2 | KhulnaSouth_230kV | JhenaidahSouth_230kV | 96 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
JhenaidahSouth_230kVtoBheramaraHVDC_230kV_Line1 | JhenaidahSouth_230kV | BheramaraHVDC_230kV | 80.5 | Twin AAAC
JhenaidahSouth_230kVtoBheramaraHVDC_230kV_Line2 | JhenaidahSouth_230kV | BheramaraHVDC_230kV | 80.5 | Twin AAAC
BoguraWest_230kVtoBarapukuria_230kV_Line1 | BoguraWest_230kV | Barapukuria_230kV | 106 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
BoguraWest_230kVtoBarapukuria_230kV_Line2 | BoguraWest_230kV | Barapukuria_230kV | 106 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
BoguraSouth_230kVtoBoguraWest_230kV_Line1 | BoguraSouth_230kV | BoguraWest_230kV | 11 | Twin AAAC
BoguraSouth_230kVtoBoguraWest_230kV_Line2 | BoguraSouth_230kV | BoguraWest_230kV | 11 | Twin AAAC
BoguraSouth_230kVtoBoguraWest_230kV_Line3 | BoguraSouth_230kV | BoguraWest_230kV | 11 | Twin AAAC
BoguraSouth_230kVtoBoguraWest_230kV_Line4 | BoguraSouth_230kV | BoguraWest_230kV | 11 | Twin AAAC
SirajganjSouthWest_230kVtoBoguraSouth_230kV_Line1 | SirajganjSouthWest_230kV | BoguraSouth_230kV | 72.5 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
SirajganjSouthWest_230kVtoBoguraSouth_230kV_Line2 | SirajganjSouthWest_230kV | BoguraSouth_230kV | 72.5 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Ishwardi_230kVtoBaghabari_230kV_Line1 | Ishwardi_230kV | Baghabari_230kV | 55 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Ishwardi_230kVtoBaghabari_230kV_Line2 | Ishwardi_230kV | Baghabari_230kV | 55 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Baghabari_230kVtoSirajganjSouthWest_230kV_Line1 | Baghabari_230kV | SirajganjSouthWest_230kV | 38 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Baghabari_230kVtoSirajganjSouthWest_230kV_Line2 | Baghabari_230kV | SirajganjSouthWest_230kV | 38 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Fenchuganj_230kVtoBibiyana_230kV_Line1 | Fenchuganj_230kV | Bibiyana_230kV | 33.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Fenchuganj_230kVtoBibiyana_230kV_Line2 | Fenchuganj_230kV | Bibiyana_230kV | 33.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Bibiyana_230kVtoShahjibazar_230kV_Line1 | Bibiyana_230kV | Shahjibazar_230kV | 95 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Bibiyana_230kVtoShahjibazar_230kV_Line2 | Bibiyana_230kV | Shahjibazar_230kV | 95 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Shahjibazar_230kVtoCumillaNorth_230kV_Line1 | Shahjibazar_230kV | CumillaNorth_230kV | 58.5 | Twin Mallard
Shahjibazar_230kVtoCumillaNorth_230kV_Line2 | Shahjibazar_230kV | CumillaNorth_230kV | 58.5 | Twin Mallard
Aminbazar_230kVtoAgargaon_230kV_Line1 | Aminbazar_230kV | Agargaon_230kV | 7.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Aminbazar_230kVtoAgargaon_230kV_Line2 | Aminbazar_230kV | Agargaon_230kV | 7.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Siddhirganj_230kVtoManiknagar_230kV_Line1 | Siddhirganj_230kV | Maniknagar_230kV | 11 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Siddhirganj_230kVtoManiknagar_230kV_Line2 | Siddhirganj_230kV | Maniknagar_230kV | 11 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
BarishalNorth_230kVtoBorhanuddin_230kV_Line1 | BarishalNorth_230kV | Borhanuddin_230kV | 62.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
BarishalNorth_230kVtoBorhanuddin_230kV_Line2 | BarishalNorth_230kV | Borhanuddin_230kV | 62.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
BheramaraHVDC_230kVtoBheramara_230kV_Line1 | BheramaraHVDC_230kV | Bheramara_230kV | 6 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
BheramaraHVDC_230kVtoBheramara_230kV_Line2 | BheramaraHVDC_230kV | Bheramara_230kV | 6 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 230
Haripur_230kVtoSiddhirganj_230kV_Line1 | Haripur_230kV | Siddhirganj_230kV | 1.65 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Haripur_230kVtoSiddhirganj_230kV_Line2 | Haripur_230kV | Siddhirganj_230kV | 1.65 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
BheramaraHVDC_230kVtoIshwardi_230kV_Line1 | BheramaraHVDC_230kV | Ishwardi_230kV | 12.8 | Quad Mallard | 0.022077 | 0.078468 | 2.7491e-05 | 230
BheramaraHVDC_230kVtoIshwardi_230kV_Line2 | BheramaraHVDC_230kV | Ishwardi_230kV | 12.8 | Quad Mallard | 0.022077 | 0.078468 | 2.7491e-05 | 230
Sikalbaha_230kVtoAnwara_230kV_Line1 | Sikalbaha_230kV | Anwara_230kV | 17.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Sikalbaha_230kVtoAnwara_230kV_Line2 | Sikalbaha_230kV | Anwara_230kV | 17.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Patuakhali_132kVtoPayra_132kV_Line1 | Patuakhali_132kV | Payra_132kV | 46.5 | Twin Mallard | 0.035324 | 0.13368 | 1.3746e-05 | 230
Patuakhali_132kVtoPayra_132kV_Line2 | Patuakhali_132kV | Payra_132kV | 46.5 | Twin Mallard | 0.035324 | 0.13368 | 1.3746e-05 | 230
RajshahiNorth_230kVtoBheramaraHVDC_230kV_Line1 | RajshahiNorth_230kV | BheramaraHVDC_230kV | 66.2 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
RajshahiNorth_230kVtoBheramaraHVDC_230kV_Line2 | RajshahiNorth_230kV | BheramaraHVDC_230kV | 66.2 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
MadunaghatNew_230kVtoHathazari_230kV_Line1 | MadunaghatNew_230kV | Hathazari_230kV | 28.35 | Quad Mallard | 0.022077 | 0.078468 | 2.7491e-05 | 230
MadunaghatNew_230kVttoHathazari_230kV_Line2 | MadunaghatNew_230kV | Hathazari_230kV | 28.35 | Quad Mallard | 0.022077 | 0.078468 | 2.7491e-05 | 230
Rampal_230kVtoKhulnaSouth_230kV_Line1 | Rampal_230kV | KhulnaSouth_230kV | 24 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Rampal_230kVtoKhulnaSouth_230kV_Line2 | Rampal_230kV | KhulnaSouth_230kV | 24 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
BarishalNorth_230kVtoGopalganjNorth_230kV_Line1 | BarishalNorth_230kV | GopalganjNorth_230kV | 75 | Twin Mallard | 0.035324 | 0.13368 | 1.3746e-05 | 230
BarishalNorth_230kVtoGopalganjNorth_230kV_Line2 | BarishalNorth_230kV | GopalganjNorth_230kV | 75 | Twin Mallard | 0.035324 | 0.13368 | 1.3746e-05 | 230
GopalganjNorth_230kVtoFaridpur_230kV_Line1 | GopalganjNorth_230kV | Faridpur_230kV | 49 | Twin Mallard | 0.035324 | 0.13368 | 1.3746e-05 | 230
GopalganjNorth_230kVtoFaridpur_230kV_Line2 | GopalganjNorth_230kV | Faridpur_230kV | 49 | Twin Mallard | 0.035324 | 0.13368 | 1.3746e-05 | 230
MadunaghatNew_230kVtoSikalbaha_230kV_Line1 | MadunaghatNew_230kV | Sikalbaha_230kV | 11.7 | Quad Mallard | 0.022077 | 0.078468 | 2.7491e-05 | 230
MadunaghatNew_230kVtoSikalbaha_230kV_Line2 | MadunaghatNew_230kV | Sikalbaha_230kV | 11.7 | Quad Mallard | 0.022077 | 0.078468 | 2.7491e-05 | 230
MadunaghatNew_230kVtoMadunaghat_230kV_Line1 | MadunaghatNew_230kV | Madunaghat_230kV | 7 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
MadunaghatNew_230kVtoMadunaghat_230kV_Line2 | MadunaghatNew_230kV | Madunaghat_230kV | 7 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
RNPP_230kVtoBaghabari_230kV_Line1 | RNPP_230kV | Baghabari_230kV | 65.5 | Twin Mallard | 0.035324 | 0.13368 | 1.3746e-05 | 230
RNPP_230kVtoBaghabari_230kV_Line2 | RNPP_230kV | Baghabari_230kV | 65.5 | Twin Mallard | 0.035324 | 0.13368 | 1.3746e-05 | 230
Khulna330MW_230kVtoKhulnaSouth_230kV_Line1 | Khulna330MW_230kV | KhulnaSouth_230kV | 14 | Twin Mallard | 0.06397 | 0.2362 | 7.1685e-06 | 230
Sonagazi_230kVtoMirsarai_230kV_Line1 | Sonagazi_230kV | Mirsarai_230kV | 13.3 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Korerhat_230kVtoChowmuhani_230kV_Line1 | Korerhat_230kV | Chowmuhani_230kV | 54 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Korerhat_230kVtoChowmuhani_230kV_Line2 | Korerhat_230kV | Chowmuhani_230kV | 54 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Korerhat_230kVtoChowmuhani_230kV_Line3 | Korerhat_230kV | Chowmuhani_230kV | 54 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Korerhat_230kVtoChowmuhani_230kV_Line4 | Korerhat_230kV | Chowmuhani_230kV | 54 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Chowmuhani_230kVtoKachua_230kV_Line1 | Chowmuhani_230kV | Kachua_230kV | 50.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Chowmuhani_230kVtoKachua_230kV_Line2 | Chowmuhani_230kV | Kachua_230kV | 50.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Chowmuhani_230kVtoKachua_230kV_Line3 | Chowmuhani_230kV | Kachua_230kV | 50.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Chowmuhani_230kVtoKachua_230kV_Line4 | Chowmuhani_230kV | Kachua_230kV | 50.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Barapukuria_230kVtoPurbasadipur_230kV_Line1 | Barapukuria_230kV | Purbasadipur_230kV | 38.7 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Barapukuria_230kVtoPurbasadipur_230kV_Line2 | Barapukuria_230kV | Purbasadipur_230kV | 38.7 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Kachua_230kVtoGazaria_230kV_Line1 | Kachua_230kV | Gazaria_230kV | 49 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Kachua_230kVtoGazaria_230kV_Line2 | Kachua_230kV | Gazaria_230kV | 49 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Kachua_230kVtoGazaria_230kV_Line3 | Kachua_230kV | Gazaria_230kV | 49 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
Kachua_230kVtoGazaria_230kV_Line4 | Kachua_230kV | Gazaria_230kV | 49 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 230
GhorashalSouthWest_230kVtoGhorashal_230kV_Line1 | GhorashalSouthWest_230kV | Ghorashal_230kV | 1.1 | XLPE 2000 sq mm | 0.015 | 0.12 | 2e-05 | 230
GhorashalSouthWest_230kVtoGhorashal_230kV_Line2 | GhorashalSouthWest_230kV | Ghorashal_230kV | 1.1 | XLPE 2000 sq mm | 0.015 | 0.12 | 2e-05 | 230
GhorashalSouthWest_230kVtoGhorashal_230kV_Line3 | GhorashalSouthWest_230kV | Ghorashal_230kV | 1.1 | XLPE 2000 sq mm | 0.015 | 0.12 | 2e-05 | 230
Shahjibazar_132kVtoBrahmanbaria_132kV_Line1 | Shahjibazar_132kV | Brahmanbaria_132kV | 57 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Shahjibazar_132kVtoBrahmanbaria_132kV_Line2 | Shahjibazar_132kV | Brahmanbaria_132kV | 57 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Brahmanbaria_132kVtoAshuganj_132kV_Line1 | Brahmanbaria_132kV | Ashuganj_132kV | 16.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Brahmanbaria_132kVtoAshuganj_132kV_Line2 | Brahmanbaria_132kV | Ashuganj_132kV | 16.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ashuganj_132kVtoGhorashal_132kV_Line1 | Ashuganj_132kV | Ghorashal_132kV | 45.5 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Ashuganj_132kVtoGhorashal_132kV_Line2 | Ashuganj_132kV | Ghorashal_132kV | 45.5 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Ghorashal_132kVtoNarsingdi_132kV_Line1 | Ghorashal_132kV | Narsingdi_132kV | 13.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ghorashal_132kVtoNarsingdi_132kV_Line2 | Ghorashal_132kV | Narsingdi_132kV | 13.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Narsingdi_132kVtoBhulta_132kV_Line1 | Narsingdi_132kV | Bhulta_132kV | 19 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Narsingdi_132kVtoBhulta_132kV_Line2 | Narsingdi_132kV | Bhulta_132kV | 19 | Grosbeak
Bhulta_132kVtoHaripur_132kV_Line1 | Bhulta_132kV | Haripur_132kV | 15 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Bhulta_132kVtoHaripur_132kV_Line2 | Bhulta_132kV | Haripur_132kV | 15 | Grosbeak
Shahjibazar_132kVtoSrimangal_132kV_Line1 | Shahjibazar_132kV | Srimangal_132kV | 36 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Shahjibazar_132kVtoSrimangal_132kV_Line2 | Shahjibazar_132kV | Srimangal_132kV | 36 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Srimangal_132kVtoFenchuganj_132kV_Line1 | Srimangal_132kV | Fenchuganj_132kV | 49 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Srimangal_132kVtoFenchuganj_132kV_Line2 | Srimangal_132kV | Fenchuganj_132kV | 49 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
FenchuganjPS_132kVtoFenchuganj_132kV_Line1 | FenchuganjPS_132kV | Fenchuganj_132kV | 3.75 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
FenchuganjPS_132kVtoFenchuganj_132kV_Line2 | FenchuganjPS_132kV | Fenchuganj_132kV | 3.75 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
FenchuganjPS_132kVtoFenchuganj_132kV_Line3 | FenchuganjPS_132kV | Fenchuganj_132kV | 3.75 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
FenchuganjPS_132kVtoFenchuganj_132kV_Line4 | FenchuganjPS_132kV | Fenchuganj_132kV | 3.75 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
FenchuganjPS_132kVtoSylhetSouth_132kV_Line1 | SylhetSouth_132kV | Fenchuganj_132kV | 5 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
SylhetSouth_132kVtoFenchuganj_132kV_Line1 | SylhetSouth_132kV | Fenchuganj_132kV | 25 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Sylhet_132kVtoSylhetSouth_132kV_Line1 | Sylhet_132kV | SylhetSouth_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sylhet_132kVtoSylhetSouth_132kV_Line2 | Sylhet_132kV | SylhetSouth_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sylhet_132kVtoChhatak_132kV_Line1 | Sylhet_132kV | Chhatak_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sylhet_132kVtoChhatak_132kV_Line2 | Sylhet_132kV | Chhatak_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kaptai_132kVtoHathazari_132kV_Line1 | Kaptai_132kV | Hathazari_132kV | 45 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kaptai_132kVtoHathazari_132kV_Line2 | Kaptai_132kV | Hathazari_132kV | 45 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Hathazari_132kVtoBaroirhat_132kV_Line1 | Hathazari_132kV | Baroirhat_132kV | 63.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Hathazari_132kVtoBaroirhat_132kV_Line2 | Hathazari_132kV | Baroirhat_132kV | 63.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Feni_132kVtoCumillaNorth_132kV_Line1 | Feni_132kV | CumillaNorth_132kV | 66 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Feni_132kVtoCumillaNorth_132kV_Line2 | Feni_132kV | CumillaNorth_132kV | 66 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaNorth_132kVtoMuradnagar_132kV_Line1 | CumillaNorth_132kV | Muradnagar_132kV | 29 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaNorth_132kVtoMuradnagar_132kV_Line2 | CumillaNorth_132kV | Muradnagar_132kV | 29 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Muradnagar_132kVtoDaudkandi_132kV_Line1 | Muradnagar_132kV | Daudkandi_132kV | 26 | Grosbeak
Muradnagar_132kVtoDaudkandi_132kV_Line2 | Muradnagar_132kV | Daudkandi_132kV | 26 | Grosbeak
Daudkandi_132kVtoSonargaon_132kV_Line1 | Daudkandi_132kV | Sonargaon_132kV | 61.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Daudkandi_132kVtoSonargaon_132kV_Line2 | Daudkandi_132kV | Sonargaon_132kV | 61.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sonargaon_132kVtoHaripur_132kV_Line1 | Sonargaon_132kV | Haripur_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sonargaon_132kVtoHaripur_132kV_Line2 | Sonargaon_132kV | Haripur_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Haripur_132kVtoSiddhirganj_132kV_Line1 | Haripur_132kV | Siddhirganj_132kV | 2.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Haripur_132kVtoSiddhirganj_132kV_Line2 | Haripur_132kV | Siddhirganj_132kV | 2.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaNorth_132kVtoKachua_132kV_Line1 | CumillaNorth_132kV | Kachua_132kV | 56 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaSouth_132kVtoKachua_132kV_Line1 | CumillaSouth_132kV | Kachua_132kV | 40 | Linnet | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kachua_132kVtoChandpur_132kV_Line1 | Kachua_132kV | Chandpur_132kV | 22 | Grosbeak
Kachua_132kVtoChandpur_132kV_Line2 | Kachua_132kV | Chandpur_132kV | 22 | Grosbeak
Ashuganj_132kVtoBajitpur_132kV_Line1 | Ashuganj_132kV | Bajitpur_132kV | 21 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Ashuganj_132kVtoBajitpur_132kV_Line2 | Ashuganj_132kV | Bajitpur_132kV | 21 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Bajitpur_132kVtoKishoreganj_132kV_Line1 | Bajitpur_132kV | Kishoreganj_132kV | 31 | Grosbeak
Bajitpur_132kVtoKishoreganj_132kV_Line2 | Bajitpur_132kV | Kishoreganj_132kV | 31 | Grosbeak
Kishoreganj_132kVtoMymensingh_132kV_Line1 | Kishoreganj_132kV | Mymensingh_132kV | 59 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kishoreganj_132kVtoMymensingh_132kV_Line2 | Kishoreganj_132kV | Mymensingh_132kV | 59 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mymensingh_132kVtoJamalpur_132kV_Line1 | Mymensingh_132kV | Jamalpur_132kV | 55 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Mymensingh_132kVtoJamalpur_132kV_Line2 | Mymensingh_132kV | Jamalpur_132kV | 55 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Madunaghat_132kVtoSikalbaha_132kV_Line1 | Madunaghat_132kV | Sikalbaha_132kV | 17 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madunaghat_132kVtoTKCCL_132kV_Line1 | Madunaghat_132kV | TKCCL_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
TKCCL_132kVtoSikalbaha_132kV_Line1 | TKCCL_132kV | Sikalbaha_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sikalbaha_132kVtoPatiya_132kV_Line1 | Sikalbaha_132kV | Patiya_132kV | 11 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Sikalbaha_132kVtoPatiya_132kV_Line2 | Sikalbaha_132kV | Patiya_132kV | 11 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Patiya_132kVtoDohazari_132kV_Line1 | Patiya_132kV | Dohazari_132kV | 21 | Grosbeak
Patiya_132kVtoDohazari_132kV_Line2 | Patiya_132kV | Dohazari_132kV | 21 | Grosbeak
Sikalbaha_132kVtoJuldah_132kV_Line1 | Sikalbaha_132kV | Juldah_132kV | 8 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Juldah_132kVtoHalishahar_132kV_Line1 | Juldah_132kV | Halishahar_132kV | 8 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Khulshi_132kVtoBaroaulia_132kV_Line1 | Khulshi_132kV | Baroaulia_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Khulshi_132kVtoAKSML_132kV_Line1 | Khulshi_132kV | AKSML_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
AKSML_132kVtoBaroaulia_132kV_Line1 | AKSML_132kV | Baroaulia_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madunaghat_132kVtoSholoshahar_132kV_Line1 | Madunaghat_132kV | Sholoshahar_132kV | 6.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madunaghat_132kVtoSholoshahar_132kV_Line2 | Madunaghat_132kV | Sholoshahar_132kV | 6.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sholoshahar_132kVtoKhulshi_132kV_Line1 | Sholoshahar_132kV | Khulshi_132kV | 6.5 | Grosbeak
Sholoshahar_132kVtoKhulshi_132kV_Line2 | Sholoshahar_132kV | Khulshi_132kV | 6.5 | Grosbeak
Kaptai_132kVtoChandraghona_132kV_Line1 | Kaptai_132kV | Chandraghona_132kV | 11.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kaptai_132kVtoChandraghona_132kV_Line2 | Kaptai_132kV | Chandraghona_132kV | 11.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chandraghona_132kVtoMadunaghat_132kV_Line1 | Chandraghona_132kV | Madunaghat_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chandraghona_132kVtoMadunaghat_132kV_Line2 | Chandraghona_132kV | Madunaghat_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madunaghat_132kVtoHathazari_132kV_Line1 | Madunaghat_132kV | Hathazari_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madunaghat_132kVtoHathazari_132kV_Line2 | Madunaghat_132kV | Hathazari_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Hathazari_132kVtoBaroaulia_132kV_Line1 | Hathazari_132kV | Baroaulia_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Hathazari_132kVtoBaroaulia_132kV_Line2 | Hathazari_132kV | Baroaulia_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Dohazari_132kVtoCox'sBazar_132kV_Line1 | Dohazari_132kV | Cox'sBazar_132kV | 87 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Dohazari_132kVtoMatarbariTConnection_132kV_Line1 | Dohazari_132kV | MatarbariTConnection_132kV | 50 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
MatarbariTConnection_132kVtoCox'sBazar_132kV_Line2 | MatarbariTConnection_132kV | Cox'sBazar_132kV | 37 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Feni_132kVtoDaganbhuiyan_132kV_Line1 | Feni_132kV | Daganbhuiyan_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Feni_132kVtoDaganbhuiyan_132kV_Line2 | Feni_132kV | Daganbhuiyan_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Daganbhuiyan_132kVtoChowmuhani_132kV_Line1 | Daganbhuiyan_132kV | Chowmuhani_132kV | 16 | Grosbeak
Daganbhuiyan_132kVtoChowmuhani_132kV_Line2 | Daganbhuiyan_132kV | Chowmuhani_132kV | 16 | Grosbeak
Baroaulia_132kVtoKSRM_132kV_Line1 | Baroaulia_132kV | KSRM_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mymensingh_132kVtoNetrokona_132kV_Line1 | Mymensingh_132kV | Netrokona_132kV | 34 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mymensingh_132kVtoNetrokona_132kV_Line2 | Mymensingh_132kV | Netrokona_132kV | 34 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
KhulnaCentral_132kVtoNoapara_132kV_Line1 | KhulnaCentral_132kV | Noapara_132kV | 23 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
KhulnaCentral_132kVtoNoapara_132kV_Line2 | KhulnaCentral_132kV | Noapara_132kV | 23 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Noapara_132kVtoJashore_132kV_Line1 | Noapara_132kV | Jashore_132kV | 28 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Noapara_132kVtoJashore_132kV_Line2 | Noapara_132kV | Jashore_132kV | 28 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Jashore_132kVtoKaliganj_132kV_Line1 | Jashore_132kV | Kaliganj_132kV | 32 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Jashore_132kVtoKaliganj_132kV_Line2 | Jashore_132kV | Kaliganj_132kV | 32 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Kaliganj_132kVtoJhenaidahSouth_132kV_Line1 | Kaliganj_132kV | JhenaidahSouth_132kV | 15.5 | AAAC 804 sq mm
Kaliganj_132kVtoJhenaidahSouth_132kV_Line2 | Kaliganj_132kV | JhenaidahSouth_132kV | 15.5 | AAAC 804 sq mm
Jhenaidah_132kVtoKushtia_132kV_Line1 | Jhenaidah_132kV | Kushtia_132kV | 43 | AAAC 804 sq mm | 0.082575 | 0.2559 | 6.5703e-06 | 132
Jhenaidah_132kVtoKushtia_132kV_Line2 | Jhenaidah_132kV | Kushtia_132kV | 43 | AAAC 804 sq mm | 0.082575 | 0.2559 | 6.5703e-06 | 132
Kushtia_132kVtoBheramara_132kV_Line1 | Kushtia_132kV | Bheramara_132kV | 23 | AAAC 804 sq mm | 0.08808 | 0.2559 | 6.5703e-06 | 132
Kushtia_132kVtoBheramara_132kV_Line2 | Kushtia_132kV | Bheramara_132kV | 23 | AAAC 804 sq mm | 0.08808 | 0.2559 | 6.5703e-06 | 132
Bheramara_132kVtoIshwardi_132kV_Line1 | Bheramara_132kV | Ishwardi_132kV | 10 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Bheramara_132kVtoIshwardi_132kV_Line2 | Bheramara_132kV | Ishwardi_132kV | 10 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Ishwardi_132kVtoNatore_132kV_Line1 | Ishwardi_132kV | Natore_132kV | 42 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Ishwardi_132kVtoNatore_132kV_Line2 | Ishwardi_132kV | Natore_132kV | 42 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Natore_132kVtoBogura_132kV_Line1 | Natore_132kV | Bogura_132kV | 61 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Natore_132kVtoBogura_132kV_Line2 | Natore_132kV | Bogura_132kV | 61 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Bogura_132kVtoMahasthangarh_132kV_Line1 | Bogura_132kV | Mahasthangarh_132kV | 10 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Bogura_132kVtoMahasthangarh_132kV_Line2 | Bogura_132kV | Mahasthangarh_132kV | 10 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Mahasthangarh_132kVtoPalashbari_132kV_Line1 | Mahasthangarh_132kV | Palashbari_132kV | 40 | AAAC 804 sq mm | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mahasthangarh_132kVtoPalashbari_132kV_Line2 | Mahasthangarh_132kV | Palashbari_132kV | 40 | AAAC 804 sq mm | 0.1101 | 0.2559 | 6.5703e-06 | 132
Palashbari_132kVtoMithapukur_132kV_Line1 | Palashbari_132kV | Mithapukur_132kV | 30 | AAAC 804 sq mm
Palashbari_132kVtoMithapukur_132kV_Line2 | Palashbari_132kV | Mithapukur_132kV | 30 | AAAC 804 sq mm
Mithapukur_132kVtoConfidencePP_132kV_Line1 | Mithapukur_132kV | ConfidencePP_132kV | 15 | AAAC 804 sq mm
Mithapukur_132kVtoConfidencePP_132kV_Line2 | Mithapukur_132kV | ConfidencePP_132kV | 15 | AAAC 804 sq mm
ConfidencePP_132kVtoRangpur_132kV_Line1 | ConfidencePP_132kV | Rangpur_132kV | 9 | AAAC 804 sq mm
ConfidencePP_132kVtoRangpur_132kV_Line2 | ConfidencePP_132kV | Rangpur_132kV | 9 | AAAC 804 sq mm
Rangpur_132kVtoTaraganj_132kV_Line1 | Rangpur_132kV | Taraganj_132kV | 19 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Rangpur_132kVtoTaraganj_132kV_Line2 | Rangpur_132kV | Taraganj_132kV | 19 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Taraganj_132kVtoSaidpur_132kV_Line1 | Taraganj_132kV | Saidpur_132kV | 21.5 | AAAC 804 sq mm
Taraganj_132kVtoSaidpur_132kV_Line2 | Taraganj_132kV | Saidpur_132kV | 21.5 | AAAC 804 sq mm
Saidpur_132kVtoPurbasadipur_132kV_Line1 | Saidpur_132kV | Purbasadipur_132kV | 24.5 | AAAC 804 sq mm | 0.08808 | 0.2559 | 6.5703e-06 | 132
Saidpur_132kVtoPurbasadipur_132kV_Line2 | Saidpur_132kV | Purbasadipur_132kV | 24.5 | AAAC 804 sq mm | 0.08808 | 0.2559 | 6.5703e-06 | 132
Purbasadipur_132kVtoThakurgaon_132kV_Line1 | Purbasadipur_132kV | Thakurgaon_132kV | 45 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Purbasadipur_132kVtoThakurgaon_132kV_Line2 | Purbasadipur_132kV | Thakurgaon_132kV | 45 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.5703e-06 | 132
Rangpur_132kVtoTeestaSolar_132kV_Line1 | Rangpur_132kV | TeestaSolar_132kV | 35.7 | Grosbeak
Rangpur_132kVtoTeestaSolar_132kV_Line2 | Rangpur_132kV | TeestaSolar_132kV | 35.7 | Grosbeak
Barishal_132kVtoBhandaria_132kV_Line1 | Barishal_132kV | Bhandaria_132kV | 49 | Hawk | 0.1466 | 0.2671 | 6.2854e-06 | 132
Bhandaria_132kVtoBagerhat_132kV_Line1 | Bhandaria_132kV | Bagerhat_132kV | 40 | Hawk | 0.1466 | 0.2671 | 6.2854e-06 | 132
Barishal_132kVtoBakerganj_132kV_Line1 | Barishal_132kV | Bakerganj_132kV | 18 | Hawk | 0.1466 | 0.2671 | 6.2854e-06 | 132
Bakerganj_132kVtoPatuakhali_132kV_Line1 | Bakerganj_132kV | Patuakhali_132kV | 20 | Hawk
Bheramara_132kVtoFaridpur_132kV_Line1 | Bheramara_132kV | Faridpur_132kV | 105 | Hawk | 0.11728 | 0.2671 | 6.2854e-06 | 132
Bheramara_132kVtoFaridpur_132kV_Line2 | Bheramara_132kV | Faridpur_132kV | 105 | Hawk | 0.11728 | 0.2671 | 6.2854e-06 | 132
Faridpur_132kVtoMadaripur_132kV_Line1 | Faridpur_132kV | Madaripur_132kV | 65.5 | Hawk | 0.1466 | 0.2671 | 6.2854e-06 | 132
Faridpur_132kVtoMadaripur_132kV_Line2 | Faridpur_132kV | Madaripur_132kV | 65.5 | Hawk | 0.1466 | 0.2671 | 6.2854e-06 | 132
Madaripur_132kVtoBarishalNorth_132kV_Line1 | Madaripur_132kV | BarishalNorth_132kV | 48.5 | Hawk | 0.1466 | 0.2671 | 6.2854e-06 | 132
Madaripur_132kVtoBarishalNorth_132kV_Line2 | Madaripur_132kV | BarishalNorth_132kV | 48.5 | Hawk | 0.1466 | 0.2671 | 6.2854e-06 | 132
BarishalNorth_132kVtoBarishal_132kV_Line1 | BarishalNorth_132kV | Barishal_132kV | 10 | Hawk | 0.11728 | 0.2671 | 6.2854e-06 | 132
BarishalNorth_132kVtoBarishal_132kV_Line2 | BarishalNorth_132kV | Barishal_132kV | 10 | Hawk | 0.11728 | 0.2671 | 6.2854e-06 | 132
Ishwardi_132kVtoBaghabari_132kV_Line1 | Ishwardi_132kV | Baghabari_132kV | 63 | Hawk | 0.1466 | 0.2671 | 6.2854e-06 | 132
Baghabari_132kVtoUllapara_132kV_Line1 | Baghabari_132kV | Ullapara_132kV | 17 | Grosbeak | 0.1466 | 0.2671 | 6.2854e-06 | 132
Shahjadpur_132kVtoUllapara_132kV_Line1 | Shahjadpur_132kV | Ullapara_132kV | 13 | Grosbeak
Ishwardi_132kVtoPabna_132kV_Line1 | Ishwardi_132kV | Pabna_132kV | 18 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Pabna_132kVtoShahjadpur_132kV_Line1 | Pabna_132kV | Shahjadpur_132kV | 41 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Bogura_132kVtoSirajganj_132kV_Line1 | Bogura_132kV | Sirajganj_132kV | 66 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Bogura_132kVtoSirajganj_132kV_Line2 | Bogura_132kV | Sirajganj_132kV | 66 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sirajganj_132kVtoShahjadpur_132kV_Line1 | Sirajganj_132kV | Shahjadpur_132kV | 34 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sirajganj_132kVtoBaghabari_132kV_Line1 | Sirajganj_132kV | Baghabari_132kV | 40 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rajshahi_132kVtoRajshahiNorth_132kV_Line1 | Rajshahi_132kV | RajshahiNorth_132kV | 48 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rajshahi_132kVtoRajshahiNorth_132kV_Line2 | Rajshahi_132kV | RajshahiNorth_132kV | 48 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rangpur_132kVtoLalmonirhat_132kV_Line1 | Rangpur_132kV | Lalmonirhat_132kV | 38 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Bogura_132kVtoNaogaon_132kV_Line1 | Bogura_132kV | Naogaon_132kV | 44 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Bogura_132kVtoNaogaon_132kV_Line2 | Bogura_132kV | Naogaon_132kV | 44 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Kabirpur_132kVtoTangail_132kV_Line1 | Kabirpur_132kV | Tangail_132kV | 51 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kabirpur_132kVtoTangail_132kV_Line2 | Kabirpur_132kV | Tangail_132kV | 51 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Tongi_132kVtoMirpur_132kV_Line1 | Tongi_132kV | Mirpur_132kV | 17 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Tongi_132kVtoUttara_132kV_Line1 | Tongi_132kV | Uttara_132kV | 15 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Uttara_132kVtoMirpur_132kV_Line1 | Uttara_132kV | Mirpur_132kV | 9 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Mirpur_132kVtoAminbazar_132kV_Line1 | Mirpur_132kV | Aminbazar_132kV | 7 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Mirpur_132kVtoAminbazar_132kV_Line2 | Mirpur_132kV | Aminbazar_132kV | 7 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Aminbazar_132kVtoKallyanpur_132kV_Line1 | Aminbazar_132kV | Kallyanpur_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Aminbazar_132kVtoKallyanpur_132kV_Line2 | Aminbazar_132kV | Kallyanpur_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kallyanpur_132kVtoLalbagh_132kV_Line1 | Kallyanpur_132kV | Lalbagh_132kV | 8 | Grosbeak
Kallyanpur_132kVtoLalbagh_132kV_Line2 | Kallyanpur_132kV | Lalbagh_132kV | 8 | Grosbeak
Lalbagh_132kVtoKeraniganj_132kV_Line1 | Lalbagh_132kV | Keraniganj_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Keraniganj_132kVtoKamrangirchar_132kV_Line1 | Keraniganj_132kVt | Kamrangirchar_132kV | 3 | Grosbeak
Kamrangirchar_132kVtoLalbagh_132kV_Line1 | Kamrangirchar_132kV | Lalbagh_132kV | 3 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Hasnabad_132kVtoKeraniganj_132kV_Line1 | Hasnabad_132kV | Keraniganj_132kV | 14 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Hasnabad_132kVtoKeraniganj_132kV_Line2 | Hasnabad_132kV | Keraniganj_132kV | 14 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Tongi_132kVtoNewTongi_132kV_Line1 | Tongi_132kV | NewTongi_132kV | 0.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Tongi_132kVtoNewTongi_132kV_Line2 | Tongi_132kV | NewTongi_132kV | 0.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Hasnabad_132kVtoSitalakhya_132kV_Line1 | Hasnabad_132kV | Sitalakhya_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madanganj_132kVtoSitalakhya_132kV_Line1 | Madanganj_132kV | Sitalakhya_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Hasnabad_132kVtoFatullah_132kV_Line1 | Hasnabad_132kV | Fatullah_132kV | 21 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Fatullah_132kVtoHaripur_132kV_Line1 | Fatullah_132kV | Haripur_132kV | 5 | Grosbeak
Madanganj_132kVtoHaripur_132kV_Line1 | Madanganj_132kV | Haripur_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Siddhirganj_132kVtoUllon_132kV_Line1 | Siddhirganj_132kV | Ullon_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Siddhirganj_132kVtoUllon_132kV_Line2 | Siddhirganj_132kV | Ullon_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Siddhirganj_132kVoMatuail_132kV_Line1 | Siddhirganj_132kV | Matuail_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Maniknagar_132kVtoMatuail_132kV_Line1 | Maniknagar_132kV | Matuail_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Siddhirganj_132kVtoManiknagar_132kV_Line1 | Siddhirganj_132kV | Maniknagar_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Maniknagar_132kVtoNarinda_132kV_Line1 | Maniknagar_132kV | Narinda_132kV | 5 | Cu 240 sq mm | 0.075 | 0.13 | 2e-05 | 132
Maniknagar_132kVtoNarinda_132kV_Line2 | Maniknagar_132kV | Narinda_132kV | 5 | Cu 240 sq mm | 0.075 | 0.13 | 2e-05 | 132
Ullon_132kVtoDhanmondi_132kV_Line1 | Ullon_132kV | Dhanmondi_132kV | 5.5 | Cu 240 sq mm | 0.075 | 0.13 | 2e-05 | 132
Ullon_132kVtoDhanmondi_132kV_Line2 | Ullon_132kV | Dhanmondi_132kV | 5.5 | Cu 240 sq mm | 0.075 | 0.13 | 2e-05 | 132
Ullon_132kVtoDhanmondi_132kV_Line3 | Ullon_132kV | Dhanmondi_132kV | 5.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Ullon_132kVtoDhanmondi_132kV_Line4 | Ullon_132kV | Dhanmondi_132kV | 5.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Tongi_132kVtoKabirpur_132kV_Line1 | Tongi_132kV | Kabirpur_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Tongi_132kVtoKabirpur_132kV_Line2 | Tongi_132kV | Kabirpur_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kabirpur_132kVtoManikganj_132kV_Line1 | Kabirpur_132kV | Manikganj_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kabirpur_132kVtoManikganj_132kV_Line2 | Kabirpur_132kV | Manikganj_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ullon_132kVtoRampura_132kV_Line1 | Ullon_132kV | Rampura_132kV | 4 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Ullon_132kVtoRampura_132kV_Line2 | Ullon_132kV | Rampura_132kV | 4 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoBashundhara_132kV_Line1 | Rampura_132kV | Bashundhara_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rampura_132kVtoBashundhara_132kV_Line2 | Rampura_132kV | Bashundhara_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Bashundhara_132kVtoTongi_132kV_Line1 | Bashundhara_132kV | Tongi_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Bashundhara_132kVtoTongi_132kV_Line2 | Bashundhara_132kV | Tongi_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rampura_132kVtoMoghbazar_132kV_Line1 | Rampura_132kV | Moghbazar_132kV | 4.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rampura_132kVtoMoghbazar_132kV_Line2 | Rampura_132kV | Moghbazar_132kV | 4.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ghorashal_132kVtoPubail_132kV_Line1 | Ghorashal_132kV | Pubail_132kV | 17.1 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ghorashal_132kVtoPubail_132kV_Line2 | Ghorashal_132kV | Pubail_132kV | 17.1 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Pubail_132kVtoJoydebpur_132kV_Line1 | Pubail_132kV | Joydebpur_132kV | 17.1 | Grosbeak
Pubail_132kVtoJoydebpur_132kV_Line2 | Pubail_132kV | Joydebpur_132kV | 17.1 | Grosbeak
Baghabari_132kVtoShahjadpur_132kV_Line1 | Baghabari_132kV | Shahjadpur_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Baghabari_132kVtoShahjadpur_132kV_Line2 | Baghabari_132kV | Shahjadpur_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chandpur_132kVtoDeshPP_132kV_Line1 | Chandpur_132kV | DeshPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chandpur_132kVtoDeshPP_132kV_Line2 | Chandpur_132kV | DeshPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
DeshPP_132kVtoRamganj_132kV_Line1 | DeshPP_132kV | Ramganj_132kV | 28 | Grosbeak
DeshPP_132kVtoRamganj_132kV_Line2 | DeshPP_132kV | Ramganj_132kV | 28 | Grosbeak
Ramganj_132kVtoChowmuhani_132kV_Line1 | Ramganj_132kV | Chowmuhani_132kV | 39 | Grosbeak
Ramganj_132kVtoChowmuhani_132kV_Line2 | Ramganj_132kV | Chowmuhani_132kV | 39 | Grosbeak
Barapukuria_132kVtoRangpur_132kV_Line1 | Barapukuria_132kV | Rangpur_132kV | 42 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Barapukuria_132kVtoRangpur_132kV_Line2 | Barapukuria_132kV | Rangpur_132kV | 42 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Barapukuria_132kVtoSaidpur_132kV_Line1 | Barapukuria_132kV | Saidpur_132kV | 36 | Grosbeak | 0.082575 | 0.2559 | 6.5703e-06 | 132
Barapukuria_132kVtoSaidpur_132kV_Line2 | Barapukuria_132kV | Saidpur_132kV | 36 | Grosbeak | 0.082575 | 0.2559 | 6.5703e-06 | 132
Madaripur_132kVtoGopalganjNorth_132kV_Line1 | Madaripur_132kV | GopalganjNorth_132kV | 23 | Grosbeak | 0.09909 | 0.2559 | 6.5703e-06 | 132
Madaripur_132kVtoGopalganjNorth_132kV_Line2 | Madaripur_132kV | GopalganjNorth_132kV | 23 | Grosbeak
Madaripur_132kVtoGopalganjNorth_132kV_Line3 | Madaripur_132kV | GopalganjNorth_132kV | 23 | Grosbeak
Madaripur_132kVtoGopalganjNorth_132kV_Line4 | Madaripur_132kV | GopalganjNorth_132kV | 23 | Grosbeak
GopalganjNorth_132kVtoGopalganj_132kV_Line1 | GopalganjNorth_132kV | Gopalganj_132kV | 35 | Grosbeak
GopalganjNorth_132kVtoGopalganj_132kV_Line2 | GopalganjNorth_132kV | Gopalganj_132kV | 35 | Grosbeak
GopalganjNorth_132kVtoFaridpur_132kV_Line1 | GopalganjNorth_132kV | Faridpur_132kV | 20 | Grosbeak
GopalganjNorth_132kVtoFaridpur_132kV_Line2 | GopalganjNorth_132kV | Faridpur_132kV | 20 | Grosbeak
Faridpur_132kVtoRajbari_132kV_Line1 | Faridpur_132kV | Rajbari_132kV | 55 | Grosbeak
Faridpur_132kVtoRajbari_132kV_Line2 | Faridpur_132kV | Rajbari_132kV | 55 | Grosbeak
Rajbari_132kVtoBheramara_132kV_Line1 | Rajbari_132kV | Bheramara_132kV | 98 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rajbari_132kVtoBheramara_132kV_Line2 | Rajbari_132kV | Bheramara_132kV | 98 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
KhulnaCentral_132kVtoKhulnaSouth_132kV_Line1 | KhulnaCentral_132kV | KhulnaSouth_132kV | 9 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 132
KhulnaCentral_132kVtoKhulnaSouth_132kV_Line2 | KhulnaCentral_132kV | KhulnaSouth_132kV | 9 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 132
KhulnaSouth_132kVtoSatkhira_132kV_Line1 | KhulnaSouth_132kV | Satkhira_132kV | 47 | Grosbeak | 0.09909 | 0.2559 | 6.5703e-06 | 132
KhulnaSouth_132kVtoSatkhira_132kV_Line2 | KhulnaSouth_132kV | Satkhira_132kV | 47 | Grosbeak | 0.09909 | 0.2559 | 6.5703e-06 | 132
Rajshahi_132kVtoNatore_132kV_Line1 | Rajshahi_132kV | Natore_132kV | 37 | Hawk | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rajshahi_132kVtoNatore_132kV_Line2 | Rajshahi_132kV | Natore_132kV | 40 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rampura_132kVtoGulshan_132kV_Line1 | Rampura_132kV | Gulshan_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoGulshan_132kV_Line2 | Rampura_132kV | Gulshan_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Sikalbaha_132kVtoBakulia_132kV_Line1 | Sikalbaha_132kV | Bakulia_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sikalbaha_132kVtoBakulia_132kV_Line2 | Sikalbaha_132kV | Bakulia_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Juldah_132kVtoShahmirpur_132kV_Line1 | Juldah_132kV | Shahmirpur_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Juldah_132kVtoShahmirpur_132kV_Line2 | Juldah_132kV | Shahmirpur_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Khulshi_132kVtoBakulia_132kV_Line1 | Khulshi_132kV | Bakulia_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Khulshi_132kVtoMSML_132kV_Line1 | Khulshi_132kV | MSML_132kV | 7.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
MSML_132kVtoBakulia_132kV_Line1 | MSML_132kV | Bakulia_132kV | 7.5 | Grosbeak
Haripur_132kVtoManiknagar_132kV_Line1 | Haripur_132kV | Maniknagar_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Joydebpur_132kVtoKodda_132kV_Line1 | Joydebpur_132kV | Kodda_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Joydebpur_132kVtoKodda_132kV_Line2 | Joydebpur_132kV | Kodda_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kodda_132kVtoKabirpur_132kV_Line1 | Kodda_132kV | Kabirpur_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kodda_132kVtoKabirpur_132kV_Line2 | Kodda_132kV | Kabirpur_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sikalbaha_132kVtoShahmirpur_132kV_Line1 | Sikalbaha_132kV | Shahmirpur_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sikalbaha_132kVtoShahmirpur_132kV_Line2 | Sikalbaha_132kV | Shahmirpur_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Khulshi_132kVtoHalishahar_132kV_Line1 | Khulshi_132kV | Halishahar_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Khulshi_132kVtoHalishahar_132kV_Line2 | Khulshi_132kV | Halishahar_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Khulshi_132kVtoRampur_132kV_Line1 | Khulshi_132kV | Rampur_132kV | 5 | Grosbeak
Khulshi_132kVtoRampur_132kV_Line2 | Khulshi_132kV | Rampur_132kV | 5 | Grosbeak
Rampur_132kVtoHalishahar_132kV_Line1 | Rampur_132kV | Halishahar_132kV | 9 | Grosbeak
Rampur_132kVtoHalishahar_132kV_Line2 | Rampur_132kV | Halishahar_132kV | 9 | Grosbeak
BoguraSouth_132kVtoBogura_132kV_Line1 | BoguraSouth_132kV | Bogura_132kV | 1.5 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 132
BoguraSouth_132kVtoBogura_132kV_Line2 | BoguraSouth_132kV | Bogura_132kV | 1.5 | Twin AAAC | 0.049545 | 0.14064 | 1.3141e-05 | 132
Ashuganj_132kVtoShahjibazar_132kV_Line1 | Ashuganj_132kV | Shahjibazar_132kV | 53 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
KhulnaSouth_132kVtoGallamari_132kV_Line1 | KhulnaSouth_132kV | Gallamari_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
KhulnaSouth_132kVtoGallamari_132kV_Line2 | KhulnaSouth_132kV | Gallamari_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Naogaon_132kVtoNiamatpur_132kV_Line1 | Naogaon_132kV | Niamatpur_132kV | 46 | Grosbeak | 0.09909 | 0.2559 | 6.5703e-06 | 132
Aminbazar_132kVtoSavar_132kV_Line1 | Aminbazar_132kV | Savar_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Aminbazar_132kVtoSavar_132kV_Line2 | Aminbazar_132kV | Savar_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Jhenaidah_132kVtoMagura_132kV_Line1 | Jhenaidah_132kV | Magura_132kV | 26.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Jhenaidah_132kVtoMagura_132kV_Line2 | Jhenaidah_132kV | Magura_132kV | 26.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Jhenaidah_132kVtoJhenaidahSouth_132kV_Line1 | Jhenaidah_132kV | JhenaidahSouth_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
JhenaidahSouth_132kVtoChuadanga_132kV_Line1 | JhenaidahSouth_132kV | Chuadanga_132kV | 39 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Thakurgaon_132kVtoPanchagarh_132kV_Line1 | Thakurgaon_132kV | Panchagarh_132kV | 45 | Grosbeak | 0.09909 | 0.2559 | 6.5703e-06 | 132
Thakurgaon_132kVtoPanchagarh_132kV_Line2 | Thakurgaon_132kV | Panchagarh_132kV | 45 | Grosbeak | 0.09909 | 0.2559 | 6.5703e-06 | 132
Sonargaon_132kVtoMeghnaghatRentalPP_132kV_Line1 | Sonargaon_132kV | MeghnaghatRentalPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sonargaon_132kVtoMeghnaghatRentalPP_132kV_Line2 | Sonargaon_132kV | MeghnaghatRentalPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Siddhirganj_132kVtoSiddhirganjDutchBanglaPP_132kV_Line1 | Siddhirganj_132kV | SiddhirganjDutchBanglaPP_132kV | 2 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Goalpara_132kVtoKhulnaCentral_132kV_Line1 | Goalpara_132kV | KhulnaCentral_132kV | 2 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
Goalpara_132kVtoKhulnaCentral_132kV_Line2 | Goalpara_132kV | KhulnaCentral_132kV | 2 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
Noapara_132kVtoNoaparaPP_132kV_Line1 | Noapara_132kV | NoaparaPP_132kV | 2 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Daudkandi_132kVtoDaudkandiPP_132kV_Line1 | Daudkandi_132kV | DaudkandiPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Gopalganj_132kVtoGopalganjPP_132kV_Line1 | Gopalganj_132kV | GopalganjPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Siddhirganj_132kVtoSiddhirganjDeshEnergyPP_132kV_Line1 | Siddhirganj_132kV | SiddhirganjDeshEnergyPP_132kV | 3 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Faridpur_132kVtoFaridpurPP_132kV_Line1 | Faridpur_132kV | FaridpurPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Baghabari_132kVtoSathia_132kV_Line1 | Baghabari_132kV | Sathia_132kV | 11 | Grosbeak
Sathia_132kVtoBeraPP_132kV_Line1 | Sathia_132kV | BeraPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
BeraPP_132kVtoIshwardi_132kV_Line1 | BeraPP_132kV | Ishwardi_132kV | 67 | Grosbeak
RajshahiNorth_132kVtoChapainawabganj_132kV_Line1 | RajshahiNorth_132kV | Chapainawabganj_132kV | 45 | Grosbeak
RajshahiNorth_132kVtoAmnura_132kV_Line1 | RajshahiNorth_132kV | Amnura_132kV | 30 | Grosbeak
Amnura_132kVtoChapainawabganj_132kV_Line1 | Amnura_132kV | Chapainawabganj_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madanganj_132kVtoMunshiganj_132kV_Line1 | Madanganj_132kV | Munshiganj_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madanganj_132kVtoMunshiganj_132kV_Line2 | Madanganj_132kV | Munshiganj_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Agargaon_132kVtoCantonment_132kV_Line1 | Agargaon_132kV | Cantonment_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Agargaon_132kVtoCantonment_132kV_Line2 | Agargaon_132kV | Cantonment_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Fenchuganj_132kVtoKulaura_132kV_Line1 | Fenchuganj_132kV | Kulaura_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Fenchuganj_132kVtoKulaura_132kV_Line2 | Fenchuganj_132kV | Kulaura_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Jamalpur_132kVtoUnitedPP_132kV_Line1 | Jamalpur_132kV | UnitedPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Jamalpur_132kVtoUnitedPP_132kV_Line2 | Jamalpur_132kV | UnitedPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
UnitedPP_132kVtoSherpur_132kV_Line1 | UnitedPP_132kV | Sherpur_132kV | 15 | Grosbeak
UnitedPP_132kVtoSherpur_132kV_Line2 | UnitedPP_132kV | Sherpur_132kV | 15 | Grosbeak
Agargaon_132kVtoSatmasjid_132kV_Line1 | Agargaon_132kV | Satmasjid_132kV | 8.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Agargaon_132kVtoSatmasjid_132kV_Line2 | Agargaon_132kV | Satmasjid_132kV | 8.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoMadartek_132kV_Line1 | Rampura_132kV | Madartek_132kV | 4.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoMadartek_132kV_Line2 | Rampura_132kV | Madartek_132kV | 4.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
CumillaNorth_132kVtoCumillaSouth_132kV_Line1 | CumillaNorth_132kV | CumillaSouth_132kV | 19 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaNorth_132kVtoCumillaSouth_132kV_Line2 | CumillaNorth_132kV | CumillaSouth_132kV | 19 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaNorth_132kVtoCumillaSouth_132kV_Line3 | CumillaNorth_132kV | CumillaSouth_132kV | 19 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Goalpara_132kVtoBagerhat_132kV_Line1 | Goalpara_132kV | Bagerhat_132kV | 45 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Goalpara_132kVtoLabancharaPP_132kV_Line1 | Goalpara_132kV | LabancharaPP_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
LabancharaPP_132kVtoBagerhat_132kV_Line1 | LabancharaPP_132kV | Bagerhat_132kV | 22.5 | Grosbeak
Kabirpur_132kVtoKaliakoir_132kV_Line1 | Kabirpur_132kV | Kaliakoir_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kabirpur_132kVtoKaliakoir_132kV_Line2 | Kabirpur_132kV | Kaliakoir_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kaliakoir_132kVtoMirzapur_132kV_Line1 | Kaliakoir_132kV | Mirzapur_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kaliakoir_132kVtoMirzapur_132kV_Line2 | Kaliakoir_132kV | Mirzapur_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mirzapur_132kVtoTangail_132kV_Line1 | Mirzapur_132kV | Tangail_132kV | 93.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mirzapur_132kVtoTangail_132kV_Line2 | Mirzapur_132kV | Tangail_132kV | 93.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Tangail_132kVtoGhatail_132kV_Line1 | Tangail_132kV | Ghatail_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Tangail_132kVtoGhatail_132kV_Line2 | Tangail_132kV | Ghatail_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ghatail_132kVtoMuktagacha_132kV_Line1 | Ghatail_132kV | Muktagacha_132kV | 42 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ghatail_132kVtoMuktagacha_132kV_Line2 | Ghatail_132kV | Muktagacha_132kV | 42 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Muktagacha_132kVtoRPCLPP_132kV_Line1 | Muktagacha_132kV | RPCLPP_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Muktagacha_132kVtoRPCLPP_132kV_Line2 | Muktagacha_132kV | RPCLPP_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
RPCLPP_132kVtoMymensingh_132kV_Line1 | RPCLPP_132kV | Mymensingh_132kV | 4 | Grosbeak
RPCLPP_132kVtoMymensingh_132kV_Line2 | RPCLPP_132kV | Mymensingh_132kV | 4 | Grosbeak
Kaliakoir_132kVtoDhamrai_132kV_Line1 | Kaliakoir_132kV | Dhamrai_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kaliakoir_132kVoDhamrai_132kV_Line2 | Kaliakoir_132kV | Dhamrai_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Dhamrai_132kVtoNabinagar_132kV_Line1 | Dhamrai_132kV | Nabinagar_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Dhamrai_132kVtoNabinagar_132kV_Line2 | Dhamrai_132kV | Nabinagar_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rangamati_132kVtoKhagrachari_132kV_Line1 | Rangamati_132kV | Khagrachari_132kV | 52.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rangamati_132kVtoKhagrachari_132kV_Line2 | Rangamati_132kV | Khagrachari_132kV | 52.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chandraghona_132kVtoRangamati_132kV_Line1 | Chandraghona_132kV | Rangamati_132kV | 27.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chandraghona_132kVtoRangamati_132kV_Line2 | Chandraghona_132kV | Rangamati_132kV | 27.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chhatak_132kVtoSunamganj_132kV_Line1 | Chhatak_132kV | Sunamganj_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chhatak_132kVtoSunamganj_132kV_Line2 | Chhatak_132kV | Sunamganj_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Beanibazar_132kVtoSylhetSouth_132kV_Line1 | Beanibazar_132kV | SylhetSouth_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Beanibazar_132kVtoSylhetSouth_132kV_Line2 | Beanibazar_132kV | SylhetSouth_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mirpur_132kVtoUttara3P_132kV_Line1 | Mirpur_132kV | Uttara3P_132kV | 5 | Grosbeak
Uttara 3P_132kVtoTongi_132kV_Line1 | Uttara 3P_132kV | Tongi_132kV | 2 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
MatarbariTConnection_132kVtoMatarbari_132kV_Line1 | MatarbariTConnection_132kV | Matarbari_132kV | 18 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Feni_132kVtoBaroirhat_132kV_Line1 | Feni_132kV | Baroirhat_132kV | 28.5 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Feni_132kVtoPHP_132kV_Line1 | Feni_132kV | PHP_132kV | 17 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
PHP_132kVtoBaroirhat_132kV_Line1 | PHP_132kV | Baroirhat_132kV | 11.5 | Grosbeak
Brahmanbaria_132kVtoNarsingdi_132kV_Line1 | Brahmanbaria_132kV | Narsingdi_132kV | 55 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Brahmanbaria_132kVtoNarsingdi_132kV_Line2 | Brahmanbaria_132kV | Narsingdi_132kV | 55 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Saidpur_132kVtoJaldhaka_132kV_Line1 | Saidpur_132kV | Jaldhaka_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Saidpur_132kVtoJaldhaka_132kV_Line2 | Saidpur_132kV | Jaldhaka_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rooppur_132kVtoIshwardi_132kV_Line1 | Rooppur_132kV | Ishwardi_132kV | 7 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rooppur_132kVtoIshwardi_132kV_Line2 | Rooppur_132kV | Ishwardi_132kV | 7 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mymensingh_132kVtoBhaluka_132kV_Line1 | Mymensingh_132kV | Bhaluka_132kV | 43 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Mymensingh_132kVtoBhaluka_132kV_Line2 | Mymensingh_132kV | Bhaluka_132kV | 43 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
MadhumatiPP_132kVtoGopalganj_132kV_Line1 | MadhumatiPP_132kV | Gopalganj_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Jashore_132kVtoBenapole_132kV_Line1 | Jashore_132kV | Benapole_132kV | 30.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Jashore_132kVtoBenapole_132kV_Line2 | Jashore_132kV | Benapole_132kV | 30.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madaripur_132kVtoShariatpur_132kV_Line1 | Madaripur_132kV | Shariatpur_132kV | 22 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Madaripur_132kVtoShariatpur_132kV_Line2 | Madaripur_132kV | Shariatpur_132kV | 22 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rangpur_132kVtoKurigram_132kV_Line1 | Rangpur_132kV | Kurigram_132kV | 41 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Magura_132kVtoNarail_132kV_Line1 | Magura_132kV | Narail_132kV | 39.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Magura_132kVtoNarail_132kV_Line2 | Magura_132kV | Narail_132kV | 39.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
BoguraSouth_132kVtoSherpur(B)_132kV_Line1 | BoguraSouth_132kV | Sherpur(B)_132kV | 24 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
BoguraSouth_132kVtoSherpur(B)_132kV_Line2 | BoguraSouth_132kV | Sherpur(B)_132kV | 24 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sherpur(B)_132kVtoSirajganj_132kV_Line1 | Sherpur(B)_132kV | Sirajganj_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sherpur(B)_132kVtoSirajganj_132kV_Line2 | Sherpur(B)_132kV | Sirajganj_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rampura_132kVtoAftabnagar_132kV_Line1 | Rampura_132kV | Aftabnagar_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoAftabnagar_132kV_Line2 | Rampura_132kV | Aftabnagar_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoHatirjheel_132kV_Line1 | Rampura_132kV | Hatirjheel_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoHatirjheel_132kV_Line2 | Rampura_132kV | Hatirjheel_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
CumillaSouth_132kVtoChauddagram_132kV_Line1 | CumillaSouth_132kV | Chauddagram_132kV | 29 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaSouth_132kVtoChauddagram_132kV_Line2 | CumillaSouth_132kV | Chauddagram_132kV | 29 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chauddagram_132kVtoFeniNorth_132kV_Line1 | Chauddagram_132kV | FeniNorth_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chauddagram_132kVtoFeniNorth_132kV_Line2 | Chauddagram_132kV | FeniNorth_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
FeniNorth_132kVtoFeni_132kV_Line1 | FeniNorth_132kV | Feni_132kV | 4 | Grosbeak
FeniNorth_132kVtoFeni_132kV_Line2 | FeniNorth_132kV | Feni_132kV | 4 | Grosbeak
Kodda_132kVtoRajendrapur_132kV_Line1 | Kodda_132kV | Rajendrapur_132kV | 24.5 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Kodda_132kVtoRajendrapur_132kV_Line2 | Kodda_132kV | Rajendrapur_132kV | 24.5 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Rampur_132kVtoAgrabad_132kV_Line1 | Rampur_132kV | Agrabad_132kV | 4.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampur_132kVtoAgrabad_132kV_Line2 | Rampur_132kV | Agrabad_132kV | 4.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Keraniganj_132kVtoSrinagar_132kV_Line1 | Keraniganj_132kV | Srinagar_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Keraniganj_132kVtoSrinagar_132kV_Line2 | Keraniganj_132kV | Srinagar_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Keraniganj_132kVtoNawabganj_132kV_Line1 | Keraniganj_132kV | Nawabganj_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Keraniganj_132kVtoNawabganj_132kV_Line2 | Keraniganj_132kV | Nawabganj_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Fatullah_132kVtoShyampur_132kV_Line1 | Fatullah_132kV | Shyampur_132kV | 4 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
Fatullah_132kVtoShyampur_132kV_Line2 | Fatullah_132kV | Shyampur_132kV | 4 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
DhakaUniversity_132kVtoDhanmondi_132kV_Line1 | DhakaUniversity_132kV | Dhanmondi_132kV | 2 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
DhakaUniversity_132kVtoDhanmondi_132kV_Line2 | DhakaUniversity_132kV | Dhanmondi_132kV | 2 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
Bagerhat_132kVtoMongla_132kV_Line1 | Bagerhat_132kV | Mongla_132kV | 28.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Bagerhat_132kVtoMongla_132kV_Line2 | Bagerhat_132kV | Mongla_132kV | 28.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Baghabari_132kVtoBhangura_132kV_Line1 | Baghabari_132kV | Bhangura_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Baghabari_132kVtoBhangura_132kV_Line2 | Baghabari_132kV | Bhangura_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Bakerganj_132kVtoBarguna_132kV_Line1 | Bakerganj_132kV | Barguna_132kV | 50 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Gallamari_132kVtoGopalganj_132kV_Line1 | Gallamari_132kV | Gopalganj_132kV | 52 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Gallamari_132kVtoGopalganj_132kV_Line2 | Gallamari_132kV | Gopalganj_132kV | 52 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Maniknagar_132kVtoKazla_132kV_Line1 | Maniknagar_132kV | Kazla_132kV | 2.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Maniknagar_132kVtoKazla_132kV_Line2 | Maniknagar_132kV | Kazla_132kV | 2.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Purbachal_132kVtoBashundhara_132kV_Line1 | Purbachal_132kV | Bashundhara_132kV | 4.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Purbachal_132kVtoBashundhara_132kV_Line2 | Purbachal_132kV | Bashundhara_132kV | 4.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Banani_132kVtoBashundhara_132kV_Line1 | Banani_132kV | Bashundhara_132kV | 13.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Banani_132kVtoBashundhara_132kV_Line2 | Banani_132kV | Bashundhara_132kV | 13.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rajbari_132kVtoBheramara_132kV_Line3 | Rajbari_132kV | Bheramara_132kV | 1.25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rajbari_132kVtoBheramara_132kV_Line4 | Rajbari_132kV | Bheramara_132kV | 1.25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Tongi_132kVtoTongi-3(Mill Gate)_132kV_Line1 | Tongi_132kV | Tongi-3(Mill Gate)_132kV | 2.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Tongi_132kVtoTongi-3(Mill Gate)_132kV_Line2 | Tongi_132kV | Tongi-3(Mill Gate)_132kV | 2.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Jhenaidah_132kVtoJhenaidahSouth_132kV_Line2 | Jhenaidah_132kV | JhenaidahSouth_132kV | 5 | Grosbeak
Jhenaidah_132kVtoJhenaidahSouth_132kV_Line3 | Jhenaidah_132kV | JhenaidahSouth_132kV | 5 | Grosbeak
JhenaidahSouth_132kVtoJashore_132kV_Line1 | JhenaidahSouth_132kV | Jashore_132kV | 43 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
JhenaidahSouth_132kVtoJashore_132kV_Line2 | JhenaidahSouth_132kV | Jashore_132kV | 43 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Maniknagar_132kVtoMotijheel_132kV_Line1 | Maniknagar_132kV | Motijheel_132kV | 2 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Maniknagar_132kVtoMotijheel_132kV_Line2 | Maniknagar_132kV | Motijheel_132kV | 2 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Motijheel_132kVtoBangabhaban_132kV_Line1 | Motijheel_132kV | Bangabhaban_132kV | 0.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Motijheel_132kVtoBangabhaban_132kV_Line2 | Motijheel_132kV | Bangabhaban_132kV | 0.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Madanganj_132kVtoCharSaidpur_132kV_Line1 | Madanganj_132kV | CharSaidpur_132kV | 3 | XLPE 800 sq mm | 0.08831 | 0.2441 | 6.8729e-06 | 132
Madanganj_132kVtoCharSaidpur_132kV_Line2 | Madanganj_132kV | CharSaidpur_132kV | 3 | XLPE 800 sq mm | 0.08831 | 0.2441 | 6.8729e-06 | 132
Kamrangirchar_132kVtoZigatola_132kV_Line1 | Kamrangirchar_132kV | Zigatola_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Kamrangirchar_132kVtoZigatola_132kV_Line2 | Kamrangirchar_132kV | Zigatola_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Energon_132kVtoMongla_132kV_Line1 | Energon_132kV | Mongla_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Hasnabad_132kVtoPostogola_132kV_Line1 | Hasnabad_132kV | Postogola_132kV | 2 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Hasnabad_132kVtoPostogola_132kV_Line2 | Hasnabad_132kV | Postogola_132kV | 2 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Banani_132kVtoPurbachal_132kV_Line1 | Banani_132kV | Purbachal_132kV | 5.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Banani_132kVtoPurbachal_132kV_Line2 | Banani_132kV | Purbachal_132kV | 5.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Chapainawabganj_132kVtoRahanpur_132kV_Line1 | Chapainawabganj_132kV | Rahanpur_132kV | 25.9 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Chapainawabganj_132kVtoRahanpur_132kV_Line2 | Chapainawabganj_132kV | Rahanpur_132kV | 25.9 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Madunaghat_132kVtoKalurghat_132kV_Line1 | Madunaghat_132kV | Kalurghat_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Madunaghat_132kVtoKalurghat_132kV_Line2 | Madunaghat_132kV | Kalurghat_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoDhakaUniversity_132kV_Line1 | Rampura_132kV | DhakaUniversity_132kV | 7.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoDhakaUniversity_132kV_Line2 | Rampura_132kV | DhakaUniversity_132kV | 7.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Sripur_132kVtoBhaluka_132kV_Line1 | Sripur_132kV | Bhaluka_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sripur_132kVtoBhaluka_132kV_Line2 | Sripur_132kV | Bhaluka_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ullapara_132kVtoSirajganj_132kV_Line1 | Ullapara_132kV | Sirajganj_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Ullapara_132kVtoSirajganj_132kV_Line2 | Ullapara_132kV | Sirajganj_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Bhaluka_132kVtoBarmiPP_132kV_Line1 | Bhaluka_132kV | BarmiPP_132kV | 32.5 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Bhaluka_132kVtoBarmiPP_132kV_Line2 | Bhaluka_132kV | BarmiPP_132kV | 32.5 | Grosbeak | 0.08808 | 0.2559 | 6.5703e-06 | 132
Niamatpur_132kVtoRahanpur_132kV_Line1 | Niamatpur_132kV | Rahanpur_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Niamatpur_132kVtoRahanpur_132kV_Line2 | Niamatpur_132kV | Rahanpur_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Naogaon_132kVtoJoypurhat_132kV_Line1 | Naogaon_132kV | Joypurhat_132kV | 47 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Naogaon_132kVtoJoypurhat_132kV_Line2 | Naogaon_132kV | Joypurhat_132kV | 47 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Cox'sBazar_132kVtoUSDKWindFarm_132kV_Line1 | Cox'sBazar_132kV | USDKWindFarm_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
BarishalNorth_132kVtoBhandaria_132kV_Line1 | BarishalNorth_132kV | Bhandaria_132kV | 46.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
BarishalNorth_132kVtoBhandaria_132kV_Line2 | BarishalNorth_132kV | Bhandaria_132kV | 46.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sirajganj68MWSolar_132kVtoSirajganj_132kV_Line1 | Sirajganj68MWSolar_132kV | Sirajganj_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sirajganj68MWSolar_132kVtoSirajganj_132kV_Line2 | Sirajganj68MWSolar_132kV | Sirajganj_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rahanpur_132kVtoChowdala_132kV_Line1 | Rahanpur_132kV | Chowdala_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rahanpur_132kVtoChowdala_132kV_Line2 | Rahanpur_132kV | Chowdala_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Muradnagar_132kVtoKasba_132kV_Line1 | Muradnagar_132kV | Kasba_132kV | 24 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Muradnagar_132kVtoKasba_132kV_Line2 | Muradnagar_132kV | Kasba_132kV | 24 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Jhenaidah_132kVtoChuadanga_132kV_Line1 | Jhenaidah_132kV | Chuadanga_132kV | 39 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kurigram_132kVtoLalmonirhat_132kV_Line1 | Kurigram_132kV | Lalmonirhat_132kV | 31 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaNorth_132kVtoChandina_132kV_Line1 | CumillaNorth_132kV | Chandina_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
CumillaNorth_132kVtoChandina_132kV_Line2 | CumillaNorth_132kV | Chandina_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rajendrapur_132kVtoSripur_132kV_Line1 | Rajendrapur_132kV | Sripur_132kV | 20.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Rajendrapur_132kVtoSripur_132kV_Line2 | Rajendrapur_132kV | Sripur_132kV | 20.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Araihazar_132kVtoBhulta_132kV_Line1 | Araihazar_132kV | Bhulta_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Araihazar_132kVtoBhulta_132kV_Line2 | Araihazar_132kV | Bhulta_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
DynamicSunSolarPP_132kVtoIshwardi_132kV_Line1 | DynamicSunSolarPP_132kV | Ishwardi_132kV | 22 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
DynamicSunSolarPP_132kVtoIshwardi_132kV_Line2 | DynamicSunSolarPP_132kV | Ishwardi_132kV | 22 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kachua_132kVtoLaksam_132kV_Line1 | Kachua_132kV | Laksam_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kachua_132kVtoLaksam_132kV_Line2 | Kachua_132kV | Laksam_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chowmuhani_132kVtoLakshmipur_132kV_Line1 | Chowmuhani_132kV | Lakshmipur_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chowmuhani_132kVtoLakshmipur_132kV_Line2 | Chowmuhani_132kV | Lakshmipur_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Chowmuhani_132kVtoMaijdee_132kV_Line1 | Chowmuhani_132kV | Maijdee_132kV | 20.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 132
Chowmuhani_132kVtoMaijdee_132kV_Line2 | Chowmuhani_132kV | Maijdee_132kV | 20.5 | Twin Mallard | 0.044155 | 0.13368 | 1.3746e-05 | 132
Sripur_132kVtoKodda_132kV_Line1 | Sripur_132kV | Kodda_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sripur_132kVtoKodda_132kV_Line2 | Sripur_132kV | Kodda_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kaliganj_132kVtoMaheshpur_132kV_Line1 | Kaliganj_132kV | Maheshpur_132kV | 26 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Kaliganj_132kVtoMaheshpur_132kV_Line2 | Kaliganj_132kV | Maheshpur_132kV | 26 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sathia_132kVtoPabna64MWSolarPP_132kV_Line1 | Sathia_132kV | Pabna64MWSolarPP_132kV | 34.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132
Sathia_132kVtoPabna64MWSolarPP_132kV_Line2 | Sathia_132kV | Pabna64MWSolarPP_132kV | 34.5 | Grosbeak | 0.1101 | 0.2559 | 6.5703e-06 | 132

## links
Row 3 contains the names of relevant pypsa variables
Link Name | Sending Bus | Receiving Bus | Limit of the Import Link (MW) | Minimum Dispatch (pu) | Marginal Cost (USD/MWh)
name | bus0 | bus1 | p_nom | p_min_pu
BheramaraHVDC_Link1 | BheramaraHVDC1_400kV_DC | BheramaraHVDC_230kV | 500 | 1
BheramaraHVDC_Link2 | BheramaraHVDC2_400kV_DC | BheramaraHVDC_230kV | 500 | 1
AdaniPP_Link1 | AdaniPPSendBus_400kV | AdaniPPRecvBus_400kV | 1435 | 1
TSECLSuryamaninagar_Link1 | SuryamaninagarSendBus_132kV | SuryamaninagarRecvBus_132kV | 192 | 1

## linedata
| Twin Bundling Factor for Res. | 0.5 |  |  |  |  | 37.7976
| Quad Bundling Factor Res. | 0.25
| Twin Bundling Factor for Ind. | 0.7 |  |  |  |  | D | 30.48 | cm
| Quad Bundling Factor Ind. | 0.55 |  |  |  |  | GMR | 1.33 | cm
| Twin Bundling Factor for Cap. | 0.5 |  |  |  |  | eps | 0
| Quad Bundling Factor Cap. | 0.22 |  |  |  |  | C | 0 | F/cm
| Operating Frequency Factor for AC Resistance |  |  | 0.92 |  |  |  | 1.7763e-06 | F/km
| Operating Frequency Factor for Ind./Cap Reactance |  |  | 0.83333 | 1.2 |  |  | 2.8421e-07 | F/mi
| Conductor Name | Res. AC 75 deg C Ohm/km | Ind. React. Ohm/km | Cap. React. MOhm/km | Susceptance | Ampacity 75 deg C
| Finch | 0.058852 | 0.19683 | 167400 | 5.9737e-06 | 1000 | XC | 1493.2999
| Twin Finch | 0.029426 | 0.13778 | 83700 | 1.1947e-05 | 2000 |  | 9333.1243
| Quad Finch | 0.014713 | 0.10826 | 36828 | 2.7153e-05 | 4000 |  | 1791.9599
| Quad Egret | 0.025346 | 0.11578 | 39811.2 | 2.5119e-05 | 2868
| Mallard | 0.081245 | 0.20342 | 174600 | 5.7274e-06 | 824
| Twin Mallard | 0.040623 | 0.14239 | 87300 | 1.1455e-05 | 1648
| Quad Mallard | 0.020311 | 0.11188 | 38412 | 2.6034e-05 | 3296 |  | 3.2431
TransPower "None" (306.6mm2) | Twin 300 sq mm | 0.044528 | 0.15272 | 92820 | 1.0774e-05 | 1370 |  | 1.6216
TransPower "Rail" (483.8mm2) | Twin AAAC 37/4.176 mm | 0.034206 | 0.14315 | 86640 | 1.1542e-05 | 1806 |  | 1.2379
TransPower "Corporant" (603.2mm2) | ACSR 600 sq mm | 0.0552 | 0.19658 | 166440 | 6.0082e-06 | 1037 |  | 19.4552
| XLPE 2000 sq mm | [6 empty] | 0.19455
| Grosbeak | 0.10129 | 0.21325 | 182640 | 5.4753e-06 | 712
| Linnet | 0.19099 | 0.23325 | 200880 | 4.9781e-06 | 478
Transpower "Faclcon" (805.7mm2) | AAAC 804 sq mm | 0.041924 | 0.18567 | 157200 | 6.3613e-06 | 1241
| Hawk | 0.13487 | 0.22258 | 190920 | 5.2378e-06 | 594
XLPE 500 sq mm
Transpower "Hawk" (241.7mm2) | Cu 240 sq mm | 0.13487 | 0.22258 | 190920 | 5.2378e-06 | 594
XLPE 800 sq mm

## gridsubs
Row 3 contains the names of relevant pypsa variables
Transformer Name | Start Bus | End Bus | Trafo Res (pu) | Trafo Reac (pu) | Nominal Capacity (MVA)
name | bus0 | bus1 | r | x | s_nom
Purbasadipur_230by132_T1 | Purbasadipur_230kV | Purbasadipur_132kV |  |  | 300
Purbasadipur_230by132_T2 | Purbasadipur_230kV | Purbasadipur_132kV |  | typical | 300
Barapukuria_230by132_T1 | Barapukuria_230kV | Barapukuria_132kV |  |  | 225
Barapukuria_230by132_T2 | Barapukuria_230kV | Barapukuria_132kV |  |  | 300
Barapukuria_230by132_T3 | Barapukuria_230kV | Barapukuria_132kV |  |  | 300
Rahanpur_400by132_T1 | Rahanpur_400kV | Rahanpur_132kV |  |  | 520
Rahanpur_400by132_T2 | Rahanpur_400kV | Rahanpur_132kV |  |  | 520
BoguraWest_400by230_T1 | BoguraWest_400kV | BoguraWest_230kV |  |  | 750
BoguraWest_400by230_T2 | BoguraWest_400kV | BoguraWest_230kV |  |  | 750
BoguraWest_400by230_T3 | BoguraWest_400kV | BoguraWest_230kV |  |  | 750
BoguraSouth_230by132_T1 | BoguraSouth_230kV | BoguraSouth_132kV |  |  | 300
BoguraSouth_230by132_T2 | BoguraSouth_230kV | BoguraSouth_132kV |  |  | 300
BoguraSouth_230by132_T3 | BoguraSouth_230kV | BoguraSouth_132kV |  |  | 225
BoguraSouth_230by132_T4 | BoguraSouth_230kV | BoguraSouth_132kV |  |  | 225
RajshahiNorth_230by132_T1 | RajshahiNorth_230kV | RajshahiNorth_132kV |  |  | 300
RajshahiNorth_230by132_T2 | RajshahiNorth_230kV | RajshahiNorth_132kV |  |  | 300
RNPP_400by230_T1 | RNPP_400kV | RNPP_230kV |  |  | 520
RNPP_400by230_T2 | RNPP_400kV | RNPP_230kV |  |  | 520
Ishwardi_230by132_T1 | Ishwardi_230kV | Ishwardi_132kV |  |  | 225
Ishwardi_230by132_T2 | Ishwardi_230kV | Ishwardi_132kV |  |  | 225
Ishwardi_230by132_T3 | Ishwardi_230kV | Ishwardi_132kV |  |  | 225
Bheramara_230by132_T1 | Bheramara_230kV | Bheramara_132kV |  |  | 225
Bheramara_230by132_T2 | Bheramara_230kV | Bheramara_132kV |  |  | 225
Baghabari_230by132_T1 | Baghabari_230kV | Baghabari_132kV |  |  | 300
Baghabari_230by132_T2 | Baghabari_230kV | Baghabari_132kV |  |  | 225
Faridpur_230by132_T1 | Faridpur_230kV | Faridpur_132kV |  |  | 350
Faridpur_230by132_T2 | Faridpur_230kV | Faridpur_132kV |  |  | 350
Jhenaidah_230by132_T1 | Jhenaidah_230kV | Jhenaidah_132kV |  |  | 300
Jhenaidah_230by132_T2 | Jhenaidah_230kV | Jhenaidah_132kV |  |  | 300
KhulnaSouth_230by132_T1 | KhulnaSouth_230kV | KhulnaSouth_132kV |  |  | 225
KhulnaSouth_230by132_T2 | KhulnaSouth_230kV | KhulnaSouth_132kV |  |  | 225
KhulnaSouth_230by132_T3 | KhulnaSouth_230kV | KhulnaSouth_132kV |  |  | 300
BarishalNorth_230by132_T1 | BarishalNorth_230kV | BarishalNorth_132kV |  |  | 300
BarishalNorth_230by132_T2 | BarishalNorth_230kV | BarishalNorth_132kV |  |  | 300
GopalganjNorth_400by230_T1 | GopalganjNorth_400kV | GopalganjNorth_230kV |  |  | 750
GopalganjNorth_400by132_T1 | GopalganjNorth_400kV | GopalganjNorth_132kV |  |  | 325
GopalganjNorth_400by132_T2 | GopalganjNorth_400kV | GopalganjNorth_132kV |  |  | 325
GopalganjNorth_400by132_T3 | GopalganjNorth_400kV | GopalganjNorth_132kV |  |  | 325
Rampal_400by230_T1 | Rampal_400kV | Rampal_230kV |  |  | 520
Rampal_400by230_T2 | Rampal_400kV | Rampal_230kV |  |  | 520
Payra_400by132_T1 | Payra_400kV | Payra_132kV |  |  | 325
Payra_400by132_T2 | Payra_400kV | Payra_132kV |  |  | 325
Kaliakoir_400by230_T1 | Kaliakoir_400kV | Kaliakoir_230kV |  |  | 520
Kaliakoir_400by230_T2 | Kaliakoir_400kV | Kaliakoir_230kV |  |  | 520
Kaliakoir_400by132_T1 | Kaliakoir_400kV | Kaliakoir_132kV |  |  | 325
Kaliakoir_400by132_T2 | Kaliakoir_400kV | Kaliakoir_132kV |  |  | 325
Kaliakoir_400by132_T3 | Kaliakoir_400kV | Kaliakoir_132kV |  |  | 325
Kaliakoir_400by132_T4 | Kaliakoir_400kV | Kaliakoir_132kV |  |  | 300
Sripur_230by132_T1 | Sripur_230kV | Sripur_132kV |  |  | 300
Sripur_230by132_T2 | Sripur_230kV | Sripur_132kV |  |  | 300
Tongi_230by132_T1 | Tongi_230kV | Tongi_132kV |  |  | 225
Tongi_230by132_T2 | Tongi_230kV | Tongi_132kV |  |  | 225
Tongi_230by132_T3 | Tongi_230kV | Tongi_132kV |  |  | 225
Ghorashal_230by132_T1 | Ghorashal_230kV | Ghorashal_132kV |  |  | 125
Ghorashal_230by132_T2 | Ghorashal_230kV | Ghorashal_132kV |  |  | 125
AshuganjNorth_400by230_T1 | AshuganjNorth_400kV | Ashuganj_230kV |  |  | 325
AshuganjNorth_400by230_T2 | AshuganjNorth_400kV | Ashuganj_230kV |  |  | 325
Ashuganj_230by132_T1 | Ashuganj_230kV | Ashuganj_132kV |  |  | 300
Ashuganj_230by132_T2 | Ashuganj_230kV | Ashuganj_132kV |  |  | 300
Bhulta_400by230_T1 | Bhulta_400kV | Bhulta_230kV |  |  | 520
Bhulta_400by230_T2 | Bhulta_400kV | Bhulta_230kV |  |  | 520
Bhulta_230by132_T1 | Bhulta_230kV | Bhulta_132kV |  |  | 300
Bhulta_230by132_T2 | Bhulta_230kV | Bhulta_132kV |  |  | 300
Aminbazar_400by230_T1 | Aminbazar_400kV | Aminbazar_230kV |  |  | 520
Aminbazar_400by230_T2 | Aminbazar_400kV | Aminbazar_230kV |  |  | 520
Aminbazar_400by230_T3 | Aminbazar_400kV | Aminbazar_230kV |  |  | 520
Aminbazar_230by132_T1 | Aminbazar_230kV | Aminbazar_132kV |  |  | 225
Aminbazar_230by132_T2 | Aminbazar_230kV | Aminbazar_132kV |  |  | 225
Aminbazar_230by132_T3 | Aminbazar_230kV | Aminbazar_132kV |  |  | 225
Keraniganj_230by132_T1 | Keraniganj_230kV | Keraniganj_132kV |  |  | 300
Keraniganj_230by132_T2 | Keraniganj_230kV | Keraniganj_132kV |  |  | 300
Keraniganj_230by132_T3 | Keraniganj_230kV | Keraniganj_132kV |  |  | 300
Agargaon_230by132_T1 | Agargaon_230kV | Agargaon_132kV |  |  | 300
Agargaon_230by132_T2 | Agargaon_230kV | Agargaon_132kV |  |  | 300
Rampura_230by132_T1 | Rampura_230kV | Rampura_132kV |  |  | 450
Rampura_230by132_T2 | Rampura_230kV | Rampura_132kV |  |  | 450
Rampura_230by132_T3 | Rampura_230kV | Rampura_132kV |  |  | 450
Maniknagar_230by132_T1 | Maniknagar_230kV | Maniknagar_132kV |  |  | 300
Maniknagar_230by132_T2 | Maniknagar_230kV | Maniknagar_132kV |  |  | 300
Hasnabad_230by132_T1 | Hasnabad_230kV | Hasnabad_132kV |  |  | 225
Hasnabad_230by132_T2 | Hasnabad_230kV | Hasnabad_132kV |  |  | 225
Hasnabad_230by132_T3 | Hasnabad_230kV | Hasnabad_132kV |  |  | 225
Shyampur_230by132_T1 | Shyampur_230kV | Shyampur_132kV |  |  | 300
Shyampur_230by132_T2 | Shyampur_230kV | Shyampur_132kV |  |  | 300
Siddhirganj_230by132_T1 | Siddhirganj_230kV | Siddhirganj_132kV |  |  | 300
Siddhirganj_230by132_T2 | Siddhirganj_230kV | Siddhirganj_132kV |  |  | 300
Haripur_230by132_T1 | Haripur_230kV | Haripur_132kV |  |  | 225
Haripur_230by132_T2 | Haripur_230kV | Haripur_132kV |  |  | 225
Haripur_230by132_T3 | Haripur_230kV | Haripur_132kV |  |  | 225
Meghnaghat_400by230_T1 | Meghnaghat_400kV | Meghnaghat_230kV |  |  | 750
Meghnaghat_400by230_T2 | Meghnaghat_400kV | Meghnaghat_230kV |  |  | 750
Meghnaghat_400by230_T3 | Meghnaghat_400kV | Meghnaghat_230kV |  |  | 750
Bibiyana_400by230_T1 | Bibiyana_400kV | Bibiyana_230kV |  |  | 520
Bibiyana_400by230_T2 | Bibiyana_400kV | Bibiyana_230kV |  |  | 520
Fenchuganj_230by132_T1 | Fenchuganj_230kV | Fenchuganj_132kV |  |  | 300
Fenchuganj_230by132_T2 | Fenchuganj_230kV | Fenchuganj_132kV |  |  | 300
CumillaNorth_230by132_T1 | CumillaNorth_230kV | CumillaNorth_132kV |  |  | 225
CumillaNorth_230by132_T2 | CumillaNorth_230kV | CumillaNorth_132kV |  |  | 225
CumillaNorth_230by132_T3 | CumillaNorth_230kV | CumillaNorth_132kV |  |  | 225
Feni_230by132_T1 | Feni_230kV | Feni_132kV |  |  | 300
Feni_230by132_T2 | Feni_230kV | Feni_132kV |  |  | 300
Kachua_230by132_T1 | Kachua_230kV | Kachua_132kV |  |  | 350
Kachua_230by132_T2 | Kachua_230kV | Kachua_132kV |  |  | 350
Hathazari_230by132_T1 | Hathazari_230kV | Hathazari_132kV |  |  | 150
Hathazari_230by132_T2 | Hathazari_230kV | Hathazari_132kV |  |  | 150
Hathazari_230by132_T3 | Hathazari_230kV | Hathazari_132kV |  |  | 150
Hathazari_230by132_T4 | Hathazari_230kV | Hathazari_132kV |  |  | 150
Korerhat_400by230_T1 | Korerhat_400kV | Korerhat_230kV |  |  | 1000
Korerhat_400by230_T2 | Korerhat_400kV | Korerhat_230kV |  |  | 1000
Chowmuhani_230by132_T1 | Chowmuhani_230kV | Chowmuhani_132kV |  |  | 350
Chowmuhani_230by132_T2 | Chowmuhani_230kV | Chowmuhani_132kV |  |  | 350
MadunaghatNew_400by230_T1 | MadunaghatNew_400kV | MadunaghatNew_230kV |  |  | 750
MadunaghatNew_400by230_T2 | MadunaghatNew_400kV | MadunaghatNew_230kV |  |  | 750
MadunaghatNew_400by230_T3 | MadunaghatNew_400kV | MadunaghatNew_230kV |  |  | 750
Madunaghat_230by132_T1 | Madunaghat_230kV | Madunaghat_132kV |  |  | 300
Madunaghat_230by132_T2 | Madunaghat_230kV | Madunaghat_132kV |  |  | 300
Madunaghat_230by132_T3 | Madunaghat_230kV | Madunaghat_132kV |  |  | 300
Sikalbaha_230by132_T1 | Sikalbaha_230kV | Sikalbaha_132kV |  |  | 300
Sikalbaha_230by132_T2 | Sikalbaha_230kV | Sikalbaha_132kV |  |  | 300
Rampur_230by132_T1 | Rampur_230kV | Rampur_132kV |  |  | 300
Rampur_230by132_T2 | Rampur_230kV | Rampur_132kV |  |  | 300

## loads
Row 3 contains the names of relevant pypsa variables
Load Name | Bus | Load Trafo MVA | Load Split Factor | Load (MW) from PGCB Report | Active Power (MW) | Reactive Power (MVar)
name | bus |  |  |  | p_set | q_set
AKSPL_230kV_Load1 | AKSPL_230kV | 150 | 0.39 |  | 5.13 | 1.69
AKSPL_230kV_Load2 | AKSPL_230kV | 150 | 0.39 |  | 5.13 | 1.69
AKSPL_230kV_Load3 | AKSPL_230kV | 80 | 0.21 |  | 2.74 | 0.9
BSRM_230kV_Load1 | BSRM_230kV | 140 | 0.5 |  | 93.5 | 30.73
BSRM_230kV_Load2 | BSRM_230kV | 140 | 0.5 |  | 93.5 | 30.73
Borhanuddin_230kV_Load1 | Borhanuddin_230kV | 140 | 0.7 |  | 49.7 | 16.34
Borhanuddin_230kV_Load2 | Borhanuddin_230kV | 60 | 0.3 |  | 21.3 | 7
GPH_230kV_Load1 | GPH_230kV | 125 | 0.5 |  | 6 | 1.97
GPH_230kV_Load2 | GPH_230kV | 125 | 0.5 |  | 6 | 1.97
GhorashalSouthWest_230kV_Load1 | GhorashalSouthWest_230kV | 140 | 1 |  | 100 | 32.87
Mirsarai_230kV_Load1 | Mirsarai_230kV | 140 | 0.5 |  | 26 | 8.55
Mirsarai_230kV_Load2 | Mirsarai_230kV | 140 | 0.5 |  | 26 | 8.55
Aftabnagar_132kV_Load1 | Aftabnagar_132kV | 120 | 0.5 |  | 21 | 6.9
Aftabnagar_132kV_Load2 | Aftabnagar_132kV | 120 | 0.5 |  | 21 | 6.9
Agargaon_132kV_Load1 | Agargaon_132kV | 120 | 0.5 |  | 61.5 | 20.21
Agargaon_132kV_Load2 | Agargaon_132kV | 120 | 0.5 |  | 61.5 | 20.21
Agrabad_132kV_Load1 | Agrabad_132kV | 120 | 0.5 |  | 27 | 8.87
Agrabad_132kV_Load2 | Agrabad_132kV | 120 | 0.5 |  | 27 | 8.87
AKSML_132kV_Load1 | AKSML_132kV | 80 | 1 |  | 6.7 | 2.2
Amnura_132kV_Load1 | Amnura_132kV | 50 | 0.33 |  | 17.33 | 5.7
Amnura_132kV_Load2 | Amnura_132kV | 50 | 0.33 |  | 17.33 | 5.7
Amnura_132kV_Load3 | Amnura_132kV | 50 | 0.33 |  | 17.33 | 5.7
Ashuganj_132kV_Load1 | Ashuganj_132kV | 75 | 0.65 |  | 62.72 | 20.61
Ashuganj_132kV_Load2 | Ashuganj_132kV | 41 | 0.35 |  | 34.28 | 11.27
Bagerhat_132kV_Load1 | Bagerhat_132kV | 41 | 0.26 |  | 20.89 | 6.87
Bagerhat_132kV_Load2 | Bagerhat_132kV | 41 | 0.26 |  | 20.89 | 6.87
Bagerhat_132kV_Load3 | Bagerhat_132kV | 75 | 0.48 |  | 38.22 | 12.56
Bajitpur_132kV_Load1 | Bajitpur_132kV | 120 | 0.5 |  | 43 | 14.13
Bajitpur_132kV_Load2 | Bajitpur_132kV | 120 | 0.5 |  | 43 | 14.13
Bakerganj_132kV_Load1 | Bakerganj_132kV | 41 | 1 |  | 13 | 4.27
Bakulia_132kV_Load1 | Bakulia_132kV | 64 | 0.23 |  | 23.25 | 7.64
Bakulia_132kV_Load2 | Bakulia_132kV | 64 | 0.23 |  | 23.25 | 7.64
Bakulia_132kV_Load3 | Bakulia_132kV | 75 | 0.27 |  | 27.25 | 8.96
Bakulia_132kV_Load4 | Bakulia_132kV | 75 | 0.27 |  | 27.25 | 8.96
Banani_132kV_Load1 | Banani_132kV | 120 | 0.5 |  | 24.6 | 8.09
Banani_132kV_Load2 | Banani_132kV | 120 | 0.5 |  | 24.6 | 8.09
Bangabhaban_132kV_Load1 | Bangabhaban_132kV | 120 | 0.77 |  | 16.26 | 5.34
Bangabhaban_132kV_Load2 | Bangabhaban_132kV | 35 | 0.23 |  | 4.74 | 1.56
Barapukuria_132kV_Load1 | Barapukuria_132kV | 41 | 0.26 |  | 16.71 | 5.49
Barapukuria_132kV_Load2 | Barapukuria_132kV | 41 | 0.26 |  | 16.71 | 5.49
Barapukuria_132kV_Load3 | Barapukuria_132kV | 75 | 0.48 |  | 30.57 | 10.05
Barguna_132kV_Load1 | Barguna_132kV | 75 | 0.5 |  | 8 | 2.63
Barguna_132kV_Load2 | Barguna_132kV | 75 | 0.5 |  | 8 | 2.63
Barishal_132kV_Load1 | Barishal_132kV | 75 | 0.38 |  | 36.92 | 12.14
Barishal_132kV_Load2 | Barishal_132kV | 120 | 0.62 |  | 59.08 | 19.42
BarishalNorth_132kV_Load1 | BarishalNorth_132kV | 120 | 0.5 |  | 43 | 14.13
BarishalNorth_132kV_Load2 | BarishalNorth_132kV | 120 | 0.5 |  | 43 | 14.13
Baroaulia_132kV_Load1 | Baroaulia_132kV | 120 | 0.5 |  | 31.5 | 10.35
Baroaulia_132kV_Load2 | Baroaulia_132kV | 120 | 0.5 |  | 31.5 | 10.35
BaroauliaSSML_132kV_Load3 | Baroaulia_132kV | 30 | 1 |  | 0 | 0
Baroirhat_132kV_Load1 | Baroirhat_132kV | 75 | 0.5 |  | 25 | 8.22
Baroirhat_132kV_Load2 | Baroirhat_132kV | 75 | 0.5 |  | 25 | 8.22
Bashundhara_132kV_Load1 | Bashundhara_132kV | 120 | 0.33 |  | 65.33 | 21.47
Bashundhara_132kV_Load2 | Bashundhara_132kV | 120 | 0.33 |  | 65.33 | 21.47
Bashundhara_132kV_Load3 | Bashundhara_132kV | 120 | 0.33 |  | 65.33 | 21.47
BashundharaCement_132kV_Load1 | Madanganj_132kV | 35 | 1 |  | 7 | 2.3
Beanibazar_132kV_Load1 | Beanibazar_132kV | 75 | 0.5 |  | 26 | 8.55
Beanibazar_132kV_Load2 | Beanibazar_132kV | 75 | 0.5 |  | 26 | 8.55
Benapole_132kV_Load1 | Benapole_132kV | 75 | 0.5 |  | 37 | 12.16
Benapole_132kV_Load2 | Benapole_132kV | 75 | 0.5 |  | 37 | 12.16
Bhaluka_132kV_Load1 | Bhaluka_132kV | 120 | 0.5 |  | 74.5 | 24.49
Bhaluka_132kV_Load2 | Bhaluka_132kV | 120 | 0.5 |  | 74.5 | 24.49
Bhandaria_132kV_Load1 | Bhandaria_132kV | 41 | 0.35 |  | 15.91 | 5.23
Bhandaria_132kV_Load2 | Bhandaria_132kV | 75 | 0.65 |  | 29.09 | 9.56
Bhangura_132kV_Load1 | Bhangura_132kV | 75 | 0.5 |  | 19.5 | 6.41
Bhangura_132kV_Load2 | Bhangura_132kV | 75 | 0.5 |  | 19.5 | 6.41
BheramaraGK_132kV_Load1 | Bheramara_132kV | 41 | 0.29 |  | 19.21 | 6.31
BheramaraGK_132kV_Load2 | Bheramara_132kV | 41 | 0.29 |  | 19.21 | 6.31
BheramaraGK_132kV_Load3 | Bheramara_132kV | 41 | 0.29 |  | 19.21 | 6.31
BheramaraGK_132kV_Load4 | Bheramara_132kV | 20 | 0.14 |  | 9.37 | 3.08
Bhulta_132kV_Load1 | Bhulta_132kV | 120 | 0.5 |  | 110.5 | 36.32
Bhulta_132kV_Load2 | Bhulta_132kV | 120 | 0.5 |  | 110.5 | 36.32
Sherpur(B)_132kV_Load1 | Sherpur(B)_132kV | 75 | 0.33 |  | 27.33 | 8.98
Sherpur(B)_132kV_Load2 | Sherpur(B)_132kV | 75 | 0.33 |  | 27.33 | 8.98
Sherpur(B)_132kV_Load3 | Sherpur(B)_132kV | 75 | 0.33 |  | 27.33 | 8.98
Bogura_132kV_Load1 | Bogura_132kV | 120 | 0.25 |  | 42.5 | 13.97
Bogura_132kV_Load2 | Bogura_132kV | 120 | 0.25 |  | 42.5 | 13.97
Bogura_132kV_Load3 | Bogura_132kV | 120 | 0.25 |  | 42.5 | 13.97
Bogura_132kV_Load4 | Bogura_132kV | 120 | 0.25 |  | 42.5 | 13.97
Brahmanbaria_132kV_Load1 | Brahmanbaria_132kV | 120 | 0.43 |  | 43.56 | 14.32
Brahmanbaria_132kV_Load2 | Brahmanbaria_132kV | 120 | 0.43 |  | 43.56 | 14.32
Brahmanbaria_132kV_Load3 | Brahmanbaria_132kV | 41 | 0.15 |  | 14.88 | 4.89
Cantonment_132kV_Load1 | Cantonment_132kV | 120 | 0.5 |  | 71 | 23.34
Cantonment_132kV_Load2 | Cantonment_132kV | 120 | 0.5 |  | 71 | 23.34
Chandina_132kV_Load1 | Chandina_132kV | 120 | 0.5 |  | 12 | 3.94
Chandina_132kV_Load2 | Chandina_132kV | 120 | 0.5 |  | 12 | 3.94
Chandpur_132kV_Load1 | Chandpur_132kV | 75 | 0.33 |  | 23.33 | 7.67
Chandpur_132kV_Load2 | Chandpur_132kV | 75 | 0.33 |  | 23.33 | 7.67
Chandpur_132kV_Load3 | Chandpur_132kV | 75 | 0.33 |  | 23.33 | 7.67
Chandraghona_132kV_Load1 | Chandraghona_132kV | 20 | 0.33 |  | 12.46 | 4.1
Chandraghona_132kV_Load2 | Chandraghona_132kV | 41 | 0.67 |  | 25.54 | 8.39
Chapainawabganj_132kV_Load1 | Chapainawabganj_132kV | 41 | 0.19 |  | 14.18 | 4.66
Chapainawabganj_132kV_Load2 | Chapainawabganj_132kV | 20 | 0.09 |  | 6.92 | 2.27
Chapainawabganj_132kV_Load3 | Chapainawabganj_132kV | 75 | 0.36 |  | 25.95 | 8.53
Chapainawabganj_132kV_Load4 | Chapainawabganj_132kV | 75 | 0.36 |  | 25.95 | 8.53
CharSaidpur_132kV_Load1 | CharSaidpur_132kV | 120 | 0.5 |  | 21.5 | 7.07
CharSaidpur_132kV_Load2 | CharSaidpur_132kV | 120 | 0.5 |  | 21.5 | 7.07
CharSaidpurShahCement_132kV_Load3 | CharSaidpur_132kV | 120 | 1 |  | 36 | 11.83
Chauddagram_132kV_Load1 | Chauddagram_132kV | 120 | 0.5 |  | 32.5 | 10.68
Chauddagram_132kV_Load2 | Chauddagram_132kV | 120 | 0.5 |  | 32.5 | 10.68
Chhatak_132kV_Load1 | Chhatak_132kV | 41 | 0.51 |  | 18.73 | 6.16
Chhatak_132kV_Load2 | Chhatak_132kV | 20 | 0.25 |  | 9.14 | 3
Chhatak_132kV_Load3 | Chhatak_132kV | 20 | 0.25 |  | 9.14 | 3
Chowmuhani_132kV_Load1 | Chowmuhani_132kV | 120 | 0.33 |  | 42 | 13.8
Chowmuhani_132kV_Load2 | Chowmuhani_132kV | 120 | 0.33 |  | 42 | 13.8
Chowmuhani_132kV_Load3 | Chowmuhani_132kV | 120 | 0.33 |  | 42 | 13.8
Chowdala_132kV_Load1 | Chowdala_132kV | 75 | 0.5 |  | 18.5 | 6.08
Chowdala_132kV_Load2 | Chowdala_132kV | 75 | 0.5 |  | 18.5 | 6.08
Chuadanga_132kV_Load1 | Chuadanga_132kV | 75 | 0.39 |  | 45.55 | 14.97
Chuadanga_132kV_Load2 | Chuadanga_132kV | 75 | 0.39 |  | 45.55 | 14.97
Chuadanga_132kV_Load3 | Chuadanga_132kV | 41 | 0.21 |  | 24.9 | 8.18
Cox'sBazar_132kV_Load1 | Cox'sBazar_132kV | 120 | 0.38 |  | 48.38 | 15.9
Cox'sBazar_132kV_Load2 | Cox'sBazar_132kV | 120 | 0.38 |  | 48.38 | 15.9
Cox'sBazar_132kV_Load3 | Cox'sBazar_132kV | 75 | 0.24 |  | 30.24 | 9.94
CumillaNorth_132kV_Load1 | CumillaNorth_132kV | 75 | 0.33 |  | 36.67 | 12.05
CumillaNorth_132kV_Load2 | CumillaNorth_132kV | 75 | 0.33 |  | 36.67 | 12.05
CumillaNorth_132kV_Load3 | CumillaNorth_132kV | 75 | 0.33 |  | 36.67 | 12.05
CumillaSouth_132kV_Load1 | CumillaSouth_132kV | 75 | 0.25 |  | 48.75 | 16.02
CumillaSouth_132kV_Load2 | CumillaSouth_132kV | 75 | 0.25 |  | 48.75 | 16.02
CumillaSouth_132kV_Load3 | CumillaSouth_132kV | 75 | 0.25 |  | 48.75 | 16.02
CumillaSouth_132kV_Load4 | CumillaSouth_132kV | 75 | 0.25 |  | 48.75 | 16.02
Daganbhuiyan_132kV_Load1 | Daganbhuiyan_132kV | 120 | 0.5 |  | 18.5 | 6.08
Daganbhuiyan_132kV_Load2 | Daganbhuiyan_132kV | 120 | 0.5 |  | 18.5 | 6.08
Daudkandi_132kV_Load1 | Daudkandi_132kV | 75 | 0.33 |  | 41.33 | 13.59
Daudkandi_132kV_Load2 | Daudkandi_132kV | 75 | 0.33 |  | 41.33 | 13.59
Daudkandi_132kV_Load3 | Daudkandi_132kV | 75 | 0.33 |  | 41.33 | 13.59
DhakaUniversity_132kV_Load1 | DhakaUniversity_132kV | 120 | 0.5 |  | 42 | 13.8
DhakaUniversity_132kV_Load2 | DhakaUniversity_132kV | 120 | 0.5 |  | 42 | 13.8
Dhamrai_132kV_Load1 | Dhamrai_132kV | 75 | 0.5 |  | 66 | 21.69
Dhamrai_132kV_Load2 | Dhamrai_132kV | 75 | 0.5 |  | 66 | 21.69
Dhanmondi_132kV_Load1 | Dhanmondi_132kV | 120 | 0.28 |  | 38.34 | 12.6
Dhanmondi_132kV_Load2 | Dhanmondi_132kV | 120 | 0.28 |  | 38.34 | 12.6
Dhanmondi_132kV_Load3 | Dhanmondi_132kV | 120 | 0.28 |  | 38.34 | 12.6
Dhanmondi_132kV_Load4 | Dhanmondi_132kV | 75 | 0.17 |  | 23.97 | 7.88
Dohazari_132kV_Load1 | Dohazari_132kV | 120 | 0.5 |  | 40.5 | 13.31
Dohazari_132kV_Load2 | Dohazari_132kV | 120 | 0.5 |  | 40.5 | 13.31
Faridpur_132kV_Load1 | Faridpur_132kV | 120 | 0.43 |  | 64.91 | 21.34
Faridpur_132kV_Load2 | Faridpur_132kV | 120 | 0.43 |  | 64.91 | 21.34
Faridpur_132kV_Load3 | Faridpur_132kV | 41 | 0.15 |  | 22.18 | 7.29
Fatullah_132kV_Load1 | Fatullah_132kV | 120 | 0.5 |  | 47 | 15.45
Fatullah_132kV_Load2 | Fatullah_132kV | 120 | 0.5 |  | 47 | 15.45
Fenchuganj_132kV_Load1 | Fenchuganj_132kV | 20 | 0.25 |  | 7.41 | 2.43
Fenchuganj_132kV_Load2 | Fenchuganj_132kV | 20 | 0.25 |  | 7.41 | 2.43
Fenchuganj_132kV_Load3 | Fenchuganj_132kV | 41 | 0.51 |  | 15.19 | 4.99
Feni_132kV_Load1 | Feni_132kV | 120 | 0.5 |  | 48 | 15.78
Feni_132kV_Load2 | Feni_132kV | 120 | 0.5 |  | 48 | 15.78
Ghatail_132kV_Load1 | Ghatail_132kV | 75 | 0.5 |  | 45 | 14.79
Ghatail_132kV_Load2 | Ghatail_132kV | 75 | 0.5 |  | 45 | 14.79
Ghorashal_132kV_Load1 | Ghorashal_132kV | 63 | 0.5 |  | 5.5 | 1.81
Ghorashal_132kV_Load2 | Ghorashal_132kV | 63 | 0.5 |  | 5.5 | 1.81
Ghorashal7Circle_132kV_Load3 | Ghorashal_132kV | 30 | 1 |  | 17.84 | 5.86
Goalpara_132kV_Load1 | Goalpara_132kV | 41 | 0.5 |  | 18 | 5.92
Goalpara_132kV_Load2 | Goalpara_132kV | 41 | 0.5 |  | 18 | 5.92
Gallamari_132kV_Load1 | Gallamari_132kV | 120 | 0.5 |  | 45 | 14.79
Gallamari_132kV_Load2 | Gallamari_132kV | 120 | 0.5 |  | 45 | 14.79
Gopalganj_132kV_Load1 | Gopalganj_132kV | 120 | 0.5 |  | 41 | 13.48
Gopalganj_132kV_Load2 | Gopalganj_132kV | 120 | 0.5 |  | 41 | 13.48
Gulshan_132kV_Load1 | Gulshan_132kV | 120 | 0.5 |  | 71 | 23.34
Gulshan_132kV_Load2 | Gulshan_132kV | 120 | 0.5 |  | 71 | 23.34
Halishahar_132kV_Load1 | Halishahar_132kV | 120 | 0.4 |  | 38.61 | 12.69
Halishahar_132kV_Load2 | Halishahar_132kV | 120 | 0.4 |  | 38.61 | 12.69
Halishahar_132kV_Load3 | Halishahar_132kV | 63 | 0.21 |  | 20.27 | 6.66
Hatirjheel_132kV_Load1 | Hatirjheel_132kV | 120 | 0.5 |  | 25.5 | 8.38
Hatirjheel_132kV_Load2 | Hatirjheel_132kV | 120 | 0.5 |  | 25.5 | 8.38
Haripur_132kV_Load1 | Haripur_132kV | 120 | 0.5 |  | 60 | 19.72
Haripur_132kV_Load2 | Haripur_132kV | 120 | 0.5 |  | 60 | 19.72
Hasnabad_132kV_Load1 | Hasnabad_132kV | 100 | 0.33 |  | 29.67 | 9.75
Hasnabad_132kV_Load2 | Hasnabad_132kV | 100 | 0.33 |  | 29.67 | 9.75
Hasnabad_132kV_Load3 | Hasnabad_132kV | 100 | 0.33 |  | 29.67 | 9.75
Hathazari_132kV_Load1 | Hathazari_132kV | 120 | 0.62 |  | 49.23 | 16.18
Hathazari_132kV_Load2 | Hathazari_132kV | 75 | 0.38 |  | 30.77 | 10.11
Ishwardi_132kV_Load1 | Ishwardi_132kV | 75 | 0.28 |  | 19.72 | 6.48
Ishwardi_132kV_Load2 | Ishwardi_132kV | 75 | 0.28 |  | 19.72 | 6.48
Ishwardi_132kV_Load3 | Ishwardi_132kV | 120 | 0.44 |  | 31.56 | 10.37
Jaldhaka_132kV_Load1 | Jaldhaka_132kV | 75 | 0.5 |  | 33.5 | 11.01
Jaldhaka_132kV_Load2 | Jaldhaka_132kV | 75 | 0.5 |  | 33.5 | 11.01
Jamalpur_132kV_Load1 | Jamalpur_132kV | 41 | 0.15 |  | 17.73 | 5.83
Jamalpur_132kV_Load2 | Jamalpur_132kV | 75 | 0.28 |  | 32.42 | 10.66
Jamalpur_132kV_Load3 | Jamalpur_132kV | 75 | 0.28 |  | 32.42 | 10.66
Jamalpur_132kV_Load4 | Jamalpur_132kV | 75 | 0.28 |  | 32.42 | 10.66
Jashore_132kV_Load1 | Jashore_132kV | 120 | 0.33 |  | 46.33 | 15.23
Jashore_132kV_Load2 | Jashore_132kV | 120 | 0.33 |  | 46.33 | 15.23
Jashore_132kV_Load3 | Jashore_132kV | 120 | 0.33 |  | 46.33 | 15.23
Jhenaidah_132kV_Load1 | Jhenaidah_132kV | 83 | 0.26 |  | 23.9 | 7.85
Jhenaidah_132kV_Load2 | Jhenaidah_132kV | 120 | 0.37 |  | 34.55 | 11.36
Jhenaidah_132kV_Load3 | Jhenaidah_132kV | 120 | 0.37 |  | 34.55 | 11.36
Joydebpur_132kV_Load1 | Joydebpur_132kV | 120 | 0.49 |  | 83.27 | 27.37
Joydebpur_132kV_Load2 | Joydebpur_132kV | 75 | 0.31 |  | 52.04 | 17.1
Joydebpur_132kV_Load3 | Joydebpur_132kV | 50 | 0.2 |  | 34.69 | 11.4
Joypurhat_132kV_Load1 | Joypurhat_132kV | 41 | 0.25 |  | 15.5 | 5.09
Joypurhat_132kV_Load2 | Joypurhat_132kV | 41 | 0.25 |  | 15.5 | 5.09
Joypurhat_132kV_Load3 | Joypurhat_132kV | 41 | 0.25 |  | 15.5 | 5.09
Joypurhat_132kV_Load4 | Joypurhat_132kV | 41 | 0.25 |  | 15.5 | 5.09
Juldah_132kV_Load1 | Juldah_132kV | 75 | 0.5 |  | 9 | 2.96
Juldah_132kV_Load2 | Juldah_132kV | 75 | 0.5 |  | 9 | 2.96
Kabirpur_132kV_Load1 | Kabirpur_132kV | 120 | 0.33 |  | 88.33 | 29.03
Kabirpur_132kV_Load2 | Kabirpur_132kV | 120 | 0.33 |  | 88.33 | 29.03
Kabirpur_132kV_Load3 | Kabirpur_132kV | 120 | 0.33 |  | 88.33 | 29.03
Kachua_132kV_Load1 | Kachua_132kV | 75 | 0.5 |  | 38.5 | 12.65
Kachua_132kV_Load2 | Kachua_132kV | 75 | 0.5 |  | 38.5 | 12.65
Kaliganj_132kV_Load1 | Kaliganj_132kV | 80 | 0.5 |  | 14 | 4.6
Kaliganj_132kV_Load2 | Kaliganj_132kV | 80 | 0.5 |  | 14 | 4.6
Kallyanpur_132kV_Load1 | Kallyanpur_132kV | 75 | 0.33 |  | 40 | 13.15
Kallyanpur_132kV_Load2 | Kallyanpur_132kV | 75 | 0.33 |  | 40 | 13.15
Kallyanpur_132kV_Load3 | Kallyanpur_132kV | 75 | 0.33 |  | 40 | 13.15
Kalurghat_132kV_Load1 | Kalurghat_132kV | 120 | 0.5 |  | 21 | 6.9
Kalurghat_132kV_Load2 | Kalurghat_132kV | 120 | 0.5 |  | 21 | 6.9
Kamrangirchar_132kV_Load1 | Kamrangirchar_132kV | 75 | 0.33 |  | 27 | 8.87
Kamrangirchar_132kV_Load2 | Kamrangirchar_132kV | 75 | 0.33 |  | 27 | 8.87
Kamrangirchar_132kV_Load3 | Kamrangirchar_132kV | 75 | 0.33 |  | 27 | 8.87
Kaptai_132kV_Load1 | Kaptai_132kV | 20 | 1 |  | 0 | 0
Kasba_132kV_Load1 | Kasba_132kV | 75 | 0.5 |  | 15.5 | 5.09
Kasba_132kV_Load2 | Kasba_132kV | 75 | 0.5 |  | 15.5 | 5.09
Kazla_132kV_Load1 | Kazla_132kV | 120 | 0.5 |  | 60.5 | 19.89
Kazla_132kV_Load2 | Kazla_132kV | 120 | 0.5 |  | 60.5 | 19.89
Keraniganj_132kV_Load1 | Keraniganj_132kV | 75 | 0.5 |  | 35.5 | 11.67
Keraniganj_132kV_Load2 | Keraniganj_132kV | 75 | 0.5 |  | 35.5 | 11.67
Khagrachari_132kV_Load1 | Khagrachari_132kV | 39 | 0.5 |  | 15 | 4.93
Khagrachari_132kV_Load2 | Khagrachari_132kV | 39 | 0.5 |  | 15 | 4.93
KhulnaCentral_132kV_Load1 | KhulnaCentral_132kV | 64 | 0.33 |  | 22.67 | 7.45
KhulnaCentral_132kV_Load2 | KhulnaCentral_132kV | 64 | 0.33 |  | 22.67 | 7.45
KhulnaCentral_132kV_Load3 | KhulnaCentral_132kV | 64 | 0.33 |  | 22.67 | 7.45
Khulshi_132kV_Load1 | Khulshi_132kV | 120 | 0.38 |  | 73.13 | 24.04
Khulshi_132kV_Load2 | Khulshi_132kV | 120 | 0.38 |  | 73.13 | 24.04
Khulshi_132kV_Load3 | Khulshi_132kV | 80 | 0.25 |  | 48.75 | 16.02
Kishoreganj_132kV_Load1 | Kishoreganj_132kV | 120 | 0.33 |  | 41.33 | 13.59
Kishoreganj_132kV_Load2 | Kishoreganj_132kV | 120 | 0.33 |  | 41.33 | 13.59
Kishoreganj_132kV_Load3 | Kishoreganj_132kV | 120 | 0.33 |  | 41.33 | 13.59
Kodda_132kV_Load1 | Kodda_132kV | 75 | 0.2 |  | 63.2 | 20.77
Kodda_132kV_Load2 | Kodda_132kV | 75 | 0.2 |  | 63.2 | 20.77
Kodda_132kV_Load3 | Kodda_132kV | 75 | 0.2 |  | 63.2 | 20.77
Kodda_132kV_Load4 | Kodda_132kV | 75 | 0.2 |  | 63.2 | 20.77
Kodda_132kV_Load5 | Kodda_132kV | 75 | 0.2 |  | 63.2 | 20.77
KSRM_132kV_Load1 | KSRM_132kV | 50 | 0.5 |  | 15 | 4.93
KSRM_132kV_Load2 | KSRM_132kV | 50 | 0.5 |  | 15 | 4.93
KSRMKYCR_132kV_Load3 | KSRM_132kV | 25 | 1 |  | 0 | 0
Kulaura_132kV_Load1 | Kulaura_132kV | 41 | 0.33 |  | 12.33 | 4.05
Kulaura_132kV_Load2 | Kulaura_132kV | 41 | 0.33 |  | 12.33 | 4.05
Kulaura_132kV_Load3 | Kulaura_132kV | 41 | 0.33 |  | 12.33 | 4.05
Kurigram_132kV_Load1 | Kurigram_132kV | 75 | 0.5 |  | 27.5 | 9.04
Kurigram_132kV_Load2 | Kurigram_132kV | 75 | 0.5 |  | 27.5 | 9.04
Kushtia_132kV_Load1 | Kushtia_132kV | 120 | 0.5 |  | 69 | 22.68
Kushtia_132kV_Load2 | Kushtia_132kV | 120 | 0.5 |  | 69 | 22.68
Laksam_132kV_Load1 | Laksam_132kV | 120 | 0.5 |  | 11 | 3.62
Laksam_132kV_Load2 | Laksam_132kV | 120 | 0.5 |  | 11 | 3.62
Lakshmipur_132kV_Load1 | Lakshmipur_132kV | 120 | 0.5 |  | 18.5 | 6.08
Lakshmipur_132kV_Load2 | Lakshmipur_132kV | 120 | 0.5 |  | 18.5 | 6.08
Lalbagh_132kV_Load1 | Lalbagh_132kV | 75 | 0.5 |  | 37 | 12.16
Lalbagh_132kV_Load2 | Lalbagh_132kV | 75 | 0.5 |  | 37 | 12.16
Lalmonirhat_132kV_Load1 | Lalmonirhat_132kV | 20 | 0.09 |  | 4.57 | 1.5
Lalmonirhat_132kV_Load2 | Lalmonirhat_132kV | 20 | 0.09 |  | 4.57 | 1.5
Lalmonirhat_132kV_Load3 | Lalmonirhat_132kV | 33 | 0.15 |  | 7.55 | 2.48
Lalmonirhat_132kV_Load4 | Lalmonirhat_132kV | 75 | 0.34 |  | 17.15 | 5.64
Lalmonirhat_132kV_Load5 | Lalmonirhat_132kV | 75 | 0.34 |  | 17.15 | 5.64
Madanganj_132kV_Load1 | Madanganj_132kV | 50 | 0.5 |  | 21 | 6.9
Madanganj_132kV_Load2 | Madanganj_132kV | 50 | 0.5 |  | 21 | 6.9
Madaripur_132kV_Load1 | Madaripur_132kV | 41 | 0.21 |  | 18.89 | 6.21
Madaripur_132kV_Load2 | Madaripur_132kV | 75 | 0.39 |  | 34.55 | 11.36
Madaripur_132kV_Load3 | Madaripur_132kV | 75 | 0.39 |  | 34.55 | 11.36
Madartek_132kV_Load1 | Madartek_132kV | 75 | 0.5 |  | 41 | 13.48
Madartek_132kV_Load2 | Madartek_132kV | 75 | 0.5 |  | 41 | 13.48
Madunaghat_132kV_Load1 | Madunaghat_132kV | 120 | 0.5 |  | 25.5 | 8.38
Madunaghat_132kV_Load2 | Madunaghat_132kV | 120 | 0.5 |  | 25.5 | 8.38
Magura_132kV_Load1 | Magura_132kV | 41 | 0.2 |  | 11.37 | 3.74
Magura_132kV_Load2 | Magura_132kV | 41 | 0.2 |  | 11.37 | 3.74
Magura_132kV_Load3 | Magura_132kV | 120 | 0.59 |  | 33.27 | 10.93
Mahasthangarh_132kV_Load1 | Mahasthangarh_132kV | 120 | 0.5 |  | 38 | 12.49
Mahasthangarh_132kV_Load2 | Mahasthangarh_132kV | 120 | 0.5 |  | 38 | 12.49
Maijdee_132kV_Load1 | Maijdee_132kV | 120 | 0.5 |  | 19.5 | 6.41
Maijdee_132kV_Load2 | Maijdee_132kV | 120 | 0.5 |  | 19.5 | 6.41
Manikganj_132kV_Load1 | Manikganj_132kV | 50 | 0.25 |  | 31.25 | 10.27
Manikganj_132kV_Load2 | Manikganj_132kV | 75 | 0.38 |  | 46.88 | 15.41
Manikganj_132kV_Load3 | Manikganj_132kV | 75 | 0.38 |  | 46.88 | 15.41
Maniknagar_132kV_Load1 | Maniknagar_132kV | 75 | 0.5 |  | 37 | 12.16
Maniknagar_132kV_Load2 | Maniknagar_132kV | 75 | 0.5 |  | 37 | 12.16
Matarbari_132kV_Load1 | Matarbari_132kV | 41 | 0.5 |  | 28 | 9.2
Matarbari_132kV_Load2 | Matarbari_132kV | 41 | 0.5 |  | 28 | 9.2
Matuail_132kV_Load1 | Matuail_132kV | 75 | 0.5 |  | 40.6 | 13.34
Matuail_132kV_Load2 | Matuail_132kV | 75 | 0.5 |  | 40.6 | 13.34
Metrorail_Motijheel_132kV_Load1 | Motijheel_132kV | 50 | 0.5 |  | 11.5 | 3.78
Metrorail_Motijheel_132kV_Load2 | Motijheel_132kV | 50 | 0.5 |  | 11.5 | 3.78
Metrorail_Uttara_132kV_Load1 | Uttara3P_132kV | 50 | 0.5 |  | 0 | 0
Metrorail_Uttara_132kV_Load2 | Uttara3P_132kV | 50 | 0.5 |  | 0 | 0
Mirpur_132kV_Load1 | Mirpur_132kV | 75 | 0.24 |  | 35.95 | 11.82
Mirpur_132kV_Load2 | Mirpur_132kV | 120 | 0.38 |  | 57.52 | 18.91
Mirpur_132kV_Load3 | Mirpur_132kV | 120 | 0.38 |  | 57.52 | 18.91
Mirzapur_132kV_Load1 | Mirzapur_132kV | 75 | 0.5 |  | 26.5 | 8.71
Mirzapur_132kV_Load2 | Mirzapur_132kV | 75 | 0.5 |  | 26.5 | 8.71
Mithapukur_132kV_Load1 | Mithapukur_132kV | 75 | 0.5 |  | 25.5 | 8.38
Mithapukur_132kV_Load2 | Mithapukur_132kV | 75 | 0.5 |  | 25.5 | 8.38
MI_Cement_132kV_Load1 | Munshiganj_132kV | 14 | 0.5 |  | 8.1 | 2.66
MI_Cement_132kV_Load2 | Munshiganj_132kV | 14 | 0.5 |  | 8.1 | 2.66
MSML_132kV_Load1 | MSML_132kV | 30 | 1 |  | 0 | 0
Moghbazar_132kV_Load1 | Moghbazar_132kV | 75 | 0.33 |  | 30.53 | 10.04
Moghbazar_132kV_Load2 | Moghbazar_132kV | 75 | 0.33 |  | 30.53 | 10.04
Moghbazar_132kV_Load3 | Moghbazar_132kV | 75 | 0.33 |  | 30.53 | 10.04
Mongla_132kV_Load1 | Mongla_132kV | 75 | 0.5 |  | 17 | 5.59
Mongla_132kV_Load2 | Mongla_132kV | 75 | 0.5 |  | 17 | 5.59
Motijheel_132kV_Load1 | Motijheel_132kV | 120 | 0.5 |  | 26 | 8.55
Motijheel_132kV_Load2 | Motijheel_132kV | 120 | 0.5 |  | 26 | 8.55
Muktagacha_132kV_Load1 | Muktagacha_132kV | 75 | 0.5 |  | 15 | 4.93
Muktagacha_132kV_Load2 | Muktagacha_132kV | 75 | 0.5 |  | 15 | 4.93
Munshiganj_132kV_Load1 | Munshiganj_132kV | 120 | 0.5 |  | 47 | 15.45
Munshiganj_132kV_Load2 | Munshiganj_132kV | 120 | 0.5 |  | 47 | 15.45
Muradnagar_132kV_Load1 | Muradnagar_132kV | 120 | 0.5 |  | 21 | 6.9
Muradnagar_132kV_Load2 | Muradnagar_132kV | 120 | 0.5 |  | 21 | 6.9
Mymensingh_132kV_Load1 | Mymensingh_132kV | 120 | 0.33 |  | 59 | 19.39
Mymensingh_132kV_Load2 | Mymensingh_132kV | 120 | 0.33 |  | 59 | 19.39
Mymensingh_132kV_Load3 | Mymensingh_132kV | 120 | 0.33 |  | 59 | 19.39
Nabinagar_132kV_Load1 | Nabinagar_132kV | 120 | 0.5 |  | 8 | 2.63
Nabinagar_132kV_Load2 | Nabinagar_132kV | 120 | 0.5 |  | 8 | 2.63
Naogaon_132kV_Load1 | Naogaon_132kV | 75 | 0.24 |  | 34.29 | 11.27
Naogaon_132kV_Load2 | Naogaon_132kV | 120 | 0.38 |  | 54.86 | 18.03
Naogaon_132kV_Load3 | Naogaon_132kV | 120 | 0.38 |  | 54.86 | 18.03
Narail_132kV_Load1 | Narail_132kV | 75 | 0.5 |  | 27 | 8.87
Narail_132kV_Load2 | Narail_132kV | 75 | 0.5 |  | 27 | 8.87
Narinda_132kV_Load1 | Narinda_132kV | 75 | 0.5 |  | 37.5 | 12.33
Narinda_132kV_Load2 | Narinda_132kV | 75 | 0.5 |  | 37.5 | 12.33
Narsingdi_132kV_Load1 | Narsingdi_132kV | 75 | 0.25 |  | 49.25 | 16.19
Narsingdi_132kV_Load2 | Narsingdi_132kV | 75 | 0.25 |  | 49.25 | 16.19
Narsingdi_132kV_Load3 | Narsingdi_132kV | 75 | 0.25 |  | 49.25 | 16.19
Narsingdi_132kV_Load4 | Narsingdi_132kV | 75 | 0.25 |  | 49.25 | 16.19
Natore_132kV_Load1 | Natore_132kV | 75 | 0.27 |  | 42.82 | 14.07
Natore_132kV_Load2 | Natore_132kV | 75 | 0.27 |  | 42.82 | 14.07
Natore_132kV_Load3 | Natore_132kV | 75 | 0.27 |  | 42.82 | 14.07
Natore_132kV_Load4 | Natore_132kV | 50 | 0.18 |  | 28.55 | 9.38
Nawabganj_132kV_Load1 | Nawabganj_132kV | 75 | 0.5 |  | 25 | 8.22
Nawabganj_132kV_Load2 | Nawabganj_132kV | 75 | 0.5 |  | 25 | 8.22
Netrokona_132kV_Load1 | Netrokona_132kV | 41 | 0.26 |  | 20.11 | 6.61
Netrokona_132kV_Load2 | Netrokona_132kV | 41 | 0.26 |  | 20.11 | 6.61
Netrokona_132kV_Load3 | Netrokona_132kV | 75 | 0.48 |  | 36.78 | 12.09
NewTongi_132kV_Load1 | NewTongi_132kV | 120 | 0.5 |  | 40 | 13.15
NewTongi_132kV_Load2 | NewTongi_132kV | 120 | 0.5 |  | 40 | 13.15
Niamatpur_132kV_Load1 | Niamatpur_132kV | 75 | 0.38 |  | 45 | 14.79
Niamatpur_132kV_Load2 | Niamatpur_132kV | 75 | 0.38 |  | 45 | 14.79
Niamatpur_132kV_Load3 | Niamatpur_132kV | 50 | 0.25 |  | 30 | 9.86
Noapara_132kV_Load1 | Noapara_132kV | 75 | 0.35 |  | 12.32 | 4.05
Noapara_132kV_Load2 | Noapara_132kV | 75 | 0.35 |  | 12.32 | 4.05
Noapara_132kV_Load3 | Noapara_132kV | 63 | 0.3 |  | 10.35 | 3.4
Pabna_132kV_Load1 | Pabna_132kV | 75 | 0.32 |  | 32.65 | 10.73
Pabna_132kV_Load2 | Pabna_132kV | 75 | 0.32 |  | 32.65 | 10.73
Pabna_132kV_Load3 | Pabna_132kV | 41 | 0.18 |  | 17.85 | 5.87
Pabna_132kV_Load4 | Pabna_132kV | 41 | 0.18 |  | 17.85 | 5.87
Palashbari_132kV_Load1 | Palashbari_132kV | 75 | 0.32 |  | 36.21 | 11.9
Palashbari_132kV_Load2 | Palashbari_132kV | 75 | 0.32 |  | 36.21 | 11.9
Palashbari_132kV_Load3 | Palashbari_132kV | 41 | 0.18 |  | 19.79 | 6.51
Palashbari_132kV_Load4 | Palashbari_132kV | 41 | 0.18 |  | 19.79 | 6.51
Panchagarh_132kV_Load1 | Panchagarh_132kV | 41 | 0.25 |  | 10.25 | 3.37
Panchagarh_132kV_Load2 | Panchagarh_132kV | 41 | 0.25 |  | 10.25 | 3.37
Panchagarh_132kV_Load3 | Panchagarh_132kV | 41 | 0.25 |  | 10.25 | 3.37
Panchagarh_132kV_Load4 | Panchagarh_132kV | 41 | 0.25 |  | 10.25 | 3.37
Patiya_132kV_Load1 | Patiya_132kV | 120 | 0.5 |  | 5.3 | 1.74
Patiya_132kV_Load2 | Patiya_132kV | 120 | 0.5 |  | 5.3 | 1.74
Patuakhali_132kV_Load1 | Patuakhali_132kV | 75 | 0.39 |  | 21.99 | 7.23
Patuakhali_132kV_Load2 | Patuakhali_132kV | 75 | 0.39 |  | 21.99 | 7.23
Patuakhali_132kV_Load3 | Patuakhali_132kV | 41 | 0.21 |  | 12.02 | 3.95
Payra_132kV_Load1 | Payra_132kV | 120 | 0.5 |  | 15 | 4.93
Payra_132kV_Load2 | Payra_132kV | 120 | 0.5 |  | 15 | 4.93
PHP_132kV_Load1 | PHP_132kV | 50 | 1 |  | 6 | 1.97
Postogola_132kV_Load1 | Postogola_132kV | 120 | 0.5 |  | 28 | 9.2
Postogola_132kV_Load2 | Postogola_132kV | 120 | 0.5 |  | 28 | 9.2
Pubail_132kV_Load1 | Pubail_132kV | 120 | 0.5 |  | 13 | 4.27
Pubail_132kV_Load2 | Pubail_132kV | 120 | 0.5 |  | 13 | 4.27
Purbachal_132kV_Load1 | Purbachal_132kV | 120 | 0.5 |  | 17 | 5.59
Purbachal_132kV_Load2 | Purbachal_132kV | 120 | 0.5 |  | 17 | 5.59
Purbasadipur_132kV_Load1 | Purbasadipur_132kV | 120 | 0.39 |  | 43.99 | 14.46
Purbasadipur_132kV_Load2 | Purbasadipur_132kV | 41 | 0.13 |  | 15.03 | 4.94
Purbasadipur_132kV_Load3 | Purbasadipur_132kV | 75 | 0.24 |  | 27.49 | 9.04
Purbasadipur_132kV_Load4 | Purbasadipur_132kV | 75 | 0.24 |  | 27.49 | 9.04
RSRM_132kV_Load1 | Haripur_132kV | 25 | 1 |  | 30 | 9.86
Rajbari_132kV_Load1 | Rajbari_132kV | 75 | 0.39 |  | 28.66 | 9.42
Rajbari_132kV_Load2 | Rajbari_132kV | 75 | 0.39 |  | 28.66 | 9.42
Rajbari_132kV_Load3 | Rajbari_132kV | 41 | 0.21 |  | 15.67 | 5.15
Rajendrapur_132kV_Load1 | Rajendrapur_132kV | 120 | 0.33 |  | 40.67 | 13.37
Rajendrapur_132kV_Load2 | Rajendrapur_132kV | 120 | 0.33 |  | 40.67 | 13.37
Rajendrapur_132kV_Load3 | Rajendrapur_132kV | 120 | 0.33 |  | 40.67 | 13.37
Rajshahi_132kV_Load1 | Rajshahi_132kV | 120 | 0.49 |  | 66.61 | 21.89
Rajshahi_132kV_Load2 | Rajshahi_132kV | 75 | 0.31 |  | 41.63 | 13.68
Rajshahi_132kV_Load3 | Rajshahi_132kV | 50 | 0.2 |  | 27.76 | 9.12
RajshahiNorth_132kV_Load1 | RajshahiNorth_132kV | 120 | 0.5 |  | 50.5 | 16.6
RajshahiNorth_132kV_Load2 | RajshahiNorth_132kV | 120 | 0.5 |  | 50.5 | 16.6
Ramganj_132kV_Load1 | Ramganj_132kV | 75 | 0.5 |  | 48 | 15.78
Ramganj_132kV_Load2 | Ramganj_132kV | 75 | 0.5 |  | 48 | 15.78
Rampur_132kV_Load1 | Rampur_132kV | 120 | 0.5 |  | 21 | 6.9
Rampur_132kV_Load2 | Rampur_132kV | 120 | 0.5 |  | 21 | 6.9
Rangamati_132kV_Load1 | Rangamati_132kV | 41 | 0.5 |  | 9.5 | 3.12
Rangamati_132kV_Load2 | Rangamati_132kV | 41 | 0.5 |  | 9.5 | 3.12
Rangpur_132kV_Load1 | Rangpur_132kV | 120 | 0.43 |  | 51.67 | 16.98
Rangpur_132kV_Load2 | Rangpur_132kV | 120 | 0.43 |  | 51.67 | 16.98
Rangpur_132kV_Load3 | Rangpur_132kV | 41 | 0.15 |  | 17.65 | 5.8
Rooppur_132kV_Load1 | Rooppur_132kV | 41 | 0.5 |  | 3.5 | 1.15
Rooppur_132kV_Load2 | Rooppur_132kV | 41 | 0.5 |  | 3.5 | 1.15
Saidpur_132kV_Load1 | Saidpur_132kV | 50 | 0.25 |  | 25.5 | 8.38
Saidpur_132kV_Load2 | Saidpur_132kV | 75 | 0.38 |  | 38.25 | 12.57
Saidpur_132kV_Load3 | Saidpur_132kV | 75 | 0.38 |  | 38.25 | 12.57
Satkhira_132kV_Load1 | Satkhira_132kV | 40 | 0.17 |  | 19.67 | 6.47
Satkhira_132kV_Load2 | Satkhira_132kV | 41 | 0.17 |  | 20.16 | 6.63
Satkhira_132kV_Load3 | Satkhira_132kV | 41 | 0.17 |  | 20.16 | 6.63
Satkhira_132kV_Load4 | Satkhira_132kV | 120 | 0.5 |  | 59.01 | 19.4
Satmasjid_132kV_Load1 | Satmasjid_132kV | 120 | 0.5 |  | 56 | 18.41
Satmasjid_132kV_Load2 | Satmasjid_132kV | 120 | 0.5 |  | 56 | 18.41
Savar_132kV_Load1 | Savar_132kV | 75 | 0.25 |  | 54.25 | 17.83
Savar_132kV_Load2 | Savar_132kV | 75 | 0.25 |  | 54.25 | 17.83
Savar_132kV_Load3 | Savar_132kV | 75 | 0.25 |  | 54.25 | 17.83
Savar_132kV_Load4 | Savar_132kV | 75 | 0.25 |  | 54.25 | 17.83
Shahjadpur_132kV_Load1 | Shahjadpur_132kV | 50 | 0.2 |  | 17 | 5.59
Shahjadpur_132kV_Load2 | Shahjadpur_132kV | 50 | 0.2 |  | 17 | 5.59
Shahjadpur_132kV_Load3 | Shahjadpur_132kV | 75 | 0.3 |  | 25.5 | 8.38
Shahjadpur_132kV_Load4 | Shahjadpur_132kV | 75 | 0.3 |  | 25.5 | 8.38
Shahjibazar_132kV_Load1 | Shahjibazar_132kV | 75 | 0.32 |  | 34.32 | 11.28
Shahjibazar_132kV_Load2 | Shahjibazar_132kV | 41 | 0.17 |  | 18.76 | 6.17
Shahjibazar_132kV_Load3 | Shahjibazar_132kV | 120 | 0.51 |  | 54.92 | 18.05
Shahmirpur_132kV_Load1 | Shahmirpur_132kV | 64 | 0.5 |  | 26 | 8.55
Shahmirpur_132kV_Load2 | Shahmirpur_132kV | 64 | 0.5 |  | 26 | 8.55
Shariatpur_132kV_Load1 | Shariatpur_132kV | 120 | 0.5 |  | 35 | 11.5
Shariatpur_132kV_Load2 | Shariatpur_132kV | 120 | 0.5 |  | 35 | 11.5
Sherpur_132kV_Load1 | Sherpur_132kV | 75 | 0.33 |  | 36.67 | 12.05
Sherpur_132kV_Load2 | Sherpur_132kV | 75 | 0.33 |  | 36.67 | 12.05
Sherpur_132kV_Load3 | Sherpur_132kV | 75 | 0.33 |  | 36.67 | 12.05
Sikalbaha_132kV_Load1 | Sikalbaha_132kV | 75 | 0.65 |  | 19.4 | 6.38
Sikalbaha_132kV_Load2 | Sikalbaha_132kV | 41 | 0.35 |  | 10.6 | 3.49
Sitalakhya_132kV_Load1 | Sitalakhya_132kV | 75 | 0.33 |  | 29.13 | 9.58
Sitalakhya_132kV_Load2 | Sitalakhya_132kV | 75 | 0.33 |  | 29.13 | 9.58
Sitalakhya_132kV_Load3 | Sitalakhya_132kV | 75 | 0.33 |  | 29.13 | 9.58
Sholoshahar_132kV_Load1 | Sholoshahar_132kV | 120 | 0.5 |  | 23 | 7.56
Sholoshahar_132kV_Load2 | Sholoshahar_132kV | 120 | 0.5 |  | 23 | 7.56
Shyampur_132kV_Load1 | Shyampur_132kV | 75 | 0.19 |  | 34.23 | 11.25
Shyampur_132kV_Load2 | Shyampur_132kV | 75 | 0.19 |  | 34.23 | 11.25
Shyampur_132kV_Load3 | Shyampur_132kV | 120 | 0.31 |  | 54.77 | 18
Shyampur_132kV_Load4 | Shyampur_132kV | 120 | 0.31 |  | 54.77 | 18
Siddhirganj_132kV_Load1 | Siddhirganj_132kV | 120 | 0.33 |  | 44 | 14.46
Siddhirganj_132kV_Load2 | Siddhirganj_132kV | 120 | 0.33 |  | 44 | 14.46
Siddhirganj_132kV_Load3 | Siddhirganj_132kV | 120 | 0.33 |  | 44 | 14.46
Sirajganj_132kV_Load1 | Sirajganj_132kV | 75 | 0.19 |  | 23.85 | 7.84
Sirajganj_132kV_Load2 | Sirajganj_132kV | 75 | 0.19 |  | 23.85 | 7.84
Sirajganj_132kV_Load3 | Sirajganj_132kV | 120 | 0.31 |  | 38.15 | 12.54
Sirajganj_132kV_Load4 | Sirajganj_132kV | 120 | 0.31 |  | 38.15 | 12.54
Sonargaon_132kV_Load1 | Sonargaon_132kV | 120 | 0.5 |  | 58.5 | 19.23
Sonargaon_132kV_Load2 | Sonargaon_132kV | 120 | 0.5 |  | 58.5 | 19.23
SonargaonBMPIL_132kV_Load3 | Sonargaon_132kV | 75 | 1 |  | 0 | 0
SonargaonTASNIM_132kV_Load4 | Sonargaon_132kV | 120 | 1 |  | 32 | 10.52
Srimangal_132kV_Load1 | Srimangal_132kV | 41 | 0.29 |  | 16.06 | 5.28
Srimangal_132kV_Load2 | Srimangal_132kV | 41 | 0.29 |  | 16.06 | 5.28
Srimangal_132kV_Load3 | Srimangal_132kV | 41 | 0.29 |  | 16.06 | 5.28
Srimangal_132kV_Load4 | Srimangal_132kV | 20 | 0.14 |  | 7.83 | 2.57
Sripur_132kV_Load1 | Sripur_132kV | 75 | 0.5 |  | 48.5 | 15.94
Sripur_132kV_Load2 | Sripur_132kV | 75 | 0.5 |  | 48.5 | 15.94
Srinagar_132kV_Load1 | Srinagar_132kV | 75 | 0.5 |  | 21.6 | 7.1
Srinagar_132kV_Load2 | Srinagar_132kV | 75 | 0.5 |  | 21.6 | 7.1
Sunamganj_132kV_Load1 | Sunamganj_132kV | 39 | 0.5 |  | 17.5 | 5.75
Sunamganj_132kV_Load2 | Sunamganj_132kV | 39 | 0.5 |  | 17.5 | 5.75
Sylhet_132kV_Load1 | Sylhet_132kV | 83.3 | 0.29 |  | 13.43 | 4.41
Sylhet_132kV_Load2 | Sylhet_132kV | 120 | 0.42 |  | 19.35 | 6.36
Sylhet_132kV_Load3 | Sylhet_132kV | 41 | 0.14 |  | 6.61 | 2.17
Sylhet_132kV_Load4 | Sylhet_132kV | 41 | 0.14 |  | 6.61 | 2.17
SylhetSouth_132kV_Load1 | SylhetSouth_132kV | 75 | 0.5 |  | 56 | 18.41
SylhetSouth_132kV_Load2 | SylhetSouth_132kV | 75 | 0.5 |  | 56 | 18.41
Tangail_132kV_Load1 | Tangail_132kV | 75 | 0.21 |  | 41.5 | 13.64
Tangail_132kV_Load2 | Tangail_132kV | 41 | 0.12 |  | 22.69 | 7.46
Tangail_132kV_Load3 | Tangail_132kV | 120 | 0.34 |  | 66.4 | 21.83
Tangail_132kV_Load4 | Tangail_132kV | 120 | 0.34 |  | 66.4 | 21.83
Taraganj_132kV_Load1 | Taraganj_132kV | 41 | 0.5 |  | 10.5 | 3.45
Taraganj_132kV_Load2 | Taraganj_132kV | 41 | 0.5 |  | 10.5 | 3.45
Thakurgaon_132kV_Load1 | Thakurgaon_132kV | 75 | 0.5 |  | 42.5 | 13.97
Thakurgaon_132kV_Load2 | Thakurgaon_132kV | 75 | 0.5 |  | 42.5 | 13.97
TKCCL_132kV_Load1 | TKCCL_132kV | 75 | 1 |  | 23.5 | 7.72
Tongi_132kV_Load1 | Tongi_132kV | 120 | 0.38 |  | 56.38 | 18.53
Tongi_132kV_Load2 | Tongi_132kV | 120 | 0.38 |  | 56.38 | 18.53
Tongi_132kV_Load3 | Tongi_132kV | 75 | 0.24 |  | 35.24 | 11.58
Tongi-3(Mill Gate)_132kV_Load1 | Tongi-3(Mill Gate)_132kV | 120 | 0.5 |  | 51.5 | 16.93
Tongi-3(Mill Gate)_132kV_Load2 | Tongi-3(Mill Gate)_132kV | 120 | 0.5 |  | 51.5 | 16.93
Ullapara_132kV_Load1 | Ullapara_132kV | 120 | 0.5 |  | 23.5 | 7.72
Ullapara_132kV_Load2 | Ullapara_132kV | 120 | 0.5 |  | 23.5 | 7.72
Ullon_132kV_Load1 | Ullon_132kV | 50 | 0.33 |  | 19 | 6.24
Ullon_132kV_Load2 | Ullon_132kV | 50 | 0.33 |  | 19 | 6.24
Ullon_132kV_Load3 | Ullon_132kV | 50 | 0.33 |  | 19 | 6.24
Uttara_132kV_Load1 | Uttara_132kV | 120 | 0.33 |  | 30.33 | 9.97
Uttara_132kV_Load2 | Uttara_132kV | 120 | 0.33 |  | 30.33 | 9.97
Uttara_132kV_Load3 | Uttara_132kV | 120 | 0.33 |  | 30.33 | 9.97
Uttara3P_132kV_Load1 | Uttara3P_132kV | 120 | 0.5 |  | 31 | 10.19
Uttara3P_132kV_Load2 | Uttara3P_132kV | 120 | 0.5 |  | 31 | 10.19
Zigatola_132kV_Load1 | Zigatola_132kV | 120 | 0.5 |  | 44.5 | 14.63
Zigatola_132kV_Load2 | Zigatola_132kV | 120 | 0.5 |  | 44.5 | 14.63

## generators
Row 3 contains the names of relevant pypsa variables
Area | Name | Technology | Fuel | Bus | Present Capacity (MW) | Marginal Cost (USD/MWh)
| name |  |  | bus | p_nom | marginal_cost
Dhaka | Ghorasal Repowered CCPP Unit-3 | CCGT |  | GhorashalSouthWest_230kV | 260
| Ghorasal Repowered CCPP Unit-4 | CCGT |  | GhorashalSouthWest_230kV | 240
| Ghorasal TPP Unit-5 | OCGT |  | GhorashalSouthWest_230kV | 190
| Ghorasal 365 MW CCPP Unit-7 | CCGT |  | GhorashalSouthWest_230kV | 365
| Ghorashal 108 MW PP (Regent) | ICE |  | GhorashalSouthWest_230kV | 97.7
| Haripur GTPP | OCGT |  | Haripur_132kV | 20
| Haripur 412 MW CCPP | CCGT |  | Haripur_132kV | 412
| Meghnaghat 450 MW CCPP (MPL) | CCGT |  | Meghnaghat_230kV | 450
| Meghnaghat CCPP(Summit) | CCGT |  | Meghnaghat_230kV | 335
| Madanganj-55 MW PP(Summit) |  |  | Madanganj_132kV | 55
| Siddhirganj 210 MW TPP |  |  | Haripur_230kV | 115
| Siddhirganj 2*120 MW GTPP |  |  | Siddhirganj_132kV | 210
| Siddhirganj 335 MW CCPP | CCGT |  | Siddhirganj_230kV | 335
| Gagnagar 102 MW PP (Digital Power) |  |  | Sitalakhya_132kV | 102
| Kamalaghat 54 MW PP(Banco Energy) |  |  | Munshiganj_132kV | 53.97
| Kodda 150 MW PP BRPL |  |  | Kodda_132kV | 149.36
| Manikganj 55 MW PP (Northern) |  |  | Savar_132kV | 55
| Nababganj 55 MW PP (Southern power ) |  |  | Hasnabad_132kV | 55
| Summit Power Ashulia |  |  | Savar_132kV | 33.75
| Summit Power Madhabdi |  |  | Narsingdi_132kV | 23
| Gazipur 52 MW PP |  |  | Kodda_132kV | 52.194
| Tongi 80 MW GTPP |  |  | Tongi_132kV | 105
| Kodda 300 MW PP Unit-2 (Summit) |  |  | Tongi_230kV | 300
| Kodda 149 MW PP Unit-1 (Summit) |  |  | Kodda_132kV | 149
| Gazipur 100 MW PP |  |  | Kodda_132kV | 105
| Meghnaghat 104 MW PP (OPCL) |  |  | Sonargaon_132kV | 104
| Manikganj 162MW PP(MPGL) |  |  | Manikganj_132kV | 162
| Spectra Solar Plant Ltd. |  |  | Manikganj_132kV | 35
| Kanchan Purbachal Power Generation Ltd. |  |  | Purbachal_132kV | 55
| Unique Meghnaghat Power Limited (UMPL) |  |  | Meghnaghat_400kV | 584
| Meghnaghat CCPP(Summit)-2 | CCGT |  | Meghnaghat_400kV | 583
| JERA Meghnaghat Power Limited |  |  | Meghnaghat_400kV | 718
| Sreepur 150 MW PP BRPL |  |  | BarmiPP_132kV | 160
Chattogram | Chattogram TPP |  |  | Raozan_230kV | 360
| Raozan 25 MW PP |  |  | Raozan_230kV | 25.5
| Teknaf 20MW PP (Solartech) |  |  | Cox'sBazar_132kV | 20
| Patenga 50MW PP (Baraka) |  |  | Halishahar_132kV | 50
| Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  |  | Kaptai_132kV | 230
| Sikalbaha 225MW CCPP |  |  | Sikalbaha_230kV | 225
| Sikalbaha Peaking GT |  |  | Sikalbaha_132kV | 150
| Sikalbaha 105 MW PP (Baraka Sikalbaha) |  |  | Sikalbaha_230kV | 105
| Hathazari 100 MW peaking PP |  |  | Hathazari_132kV | 98
| Dohazari -Kalaish 100 MW Peaking |  |  | Dohazari_132kV | 102
| Juldah 100 MW PP Unit-3 (Acorn) |  |  | Juldah_132kV | 100
| Malancha, Ctg. EPZ (United) |  |  | Halishahar_132kV | 42
| Chattogram 108 MW PP (ECPV) |  |  | Sikalbaha_132kV | 108
| Kaptai 7 MW Solar PP |  |  | Kaptai_132kV | 6
| Anwara 300 MW PP (United) |  |  | Anwara_230kV | 300
| Zodiac Power |  |  | Sikalbaha_230kV | 54.363
| Karnaphuli Power Ltd. |  |  | Sikalbaha_230kV | 110
| Juldah unit-2 (Acorn) |  |  | Juldah_132kV | 100
| Anlima Energy Ltd. |  |  | Sikalbaha_230kV | 116
| Mirsharai 150 MW BRPL |  |  | Mirsarai_230kV | 163
| SS Power |  |  | Banskhali_400kV | 1224
| Cox's Bazar Wind |  |  | USDKWindFarm_132kV | 60
| Matarbari 2*600 MW (CPGCBL) |  |  | Matarbari_400kV | 1150
Cumilla | Ashuganj CCPP 225 MW | CCGT |  | Ashuganj_132kV | 221
| Ashuganj 450 MW CCPP(North) | CCGT |  | AshuganjNorth_400kV | 350.01
| Ashuganj 450 MW CCPP(South) | CCGT |  | Ashuganj_230kV | 342.01
| Ashuganj 420 MW CCPP(East) | CCGT |  | Ashuganj_230kV | 393
| Ashuganj TSK 50 MW PP |  |  | Ashuganj_132kV | 46.701
| Ashuganj 55 MW PP (Precision) |  |  | Ashuganj_132kV | 52.824
| Ashuganj 195 MW PP (APSCL-United) |  |  | Ashuganj_230kV | 195
| Ashuganj 51 MW PP (Midland) |  |  | Ashuganj_230kV | 51
| Ashuganj 150MW PP (Midland) |  |  | Ashuganj_230kV | 150
| Titas 50 MW Peaking PP |  |  | DaudkandiPP_132kV | 52
| Chandpur 150 MW CCPP |  |  | Chandpur_132kV | 163
| Chandpur 200MW (Desh energy) |  |  | DeshPP_132kV | 200
| Jangalia 52 MW PP (Lakdanavi) |  |  | CumillaSouth_132kV | 52.2
| Cumilla 25 MW PP (Summit) |  |  | CumillaNorth_132kV | 25
| Feni Lanka Power |  |  | Feni_132kV | 114
| Chowmuhani 113 MW |  |  | Chowmuhani_132kV | 113
| Chandpur 115(Doreen) |  |  | Chandpur_132kV | 115
| Sonagazi 75 MW (AC) Solar Power Plant |  |  | Sonagazi_230kV | 75
Mymensingh | RPCL 210MW CCPP | CCGT |  | RPCLPP_132kV | 210
| Sarishabari 3 MW Solar Plant |  |  | Jamalpur_132kV | 2.71
| Mymensingh 200 MW PP (United) |  |  | UnitedPP_132kV | 200
| Jamalpur 115 MW PP (United) |  |  | UnitedPP_132kV | 115
| Sutiakhali 50 MW Solar PP |  |  | Mymensingh_132kV | 50
| Tangail Palli Power Gen 22 MW |  |  | Tangail_132kV | 22
| Bhairab 54.5 MW |  |  | Kishoreganj_132kV | 54.5
Sylhet | Moulvibazar 10 MW Solar Power Plant |  |  | Srimangal_132kV | 0
| Fenchugonj CCPP Phase-1 | CCGT |  | Fenchuganj_132kV | 90
| Fenchugonj CCPP Phase-2 | CCGT |  | Fenchuganj_132kV | 90
| Kushiara 163 MW CCPP (KP) | CCGT |  | Fenchuganj_230kV | 163
| Shajibazar 330 MW CCPP | CCGT |  | Shahjibazar_230kV | 330
| Shahjibazar GTPP Unit- 8 & 9 |  |  | Shahjibazar_132kV | 66
| Shahjibazar 86MW PP (Shahjibazar) |  |  | Shahjibazar_132kV | 86
| Shahjibazar 100 MW GTPP |  |  | Shahjibazar_132kV | 100
| Sylhet 225 MW CCPP | CCGT |  | Sylhet_132kV | 231
| Sylhet 20 MW GTPP |  |  | Sylhet_132kV | 20
| Shahjahanulla 25 MW PP |  |  | Sylhet_132kV | 25
| Bibiana-II 341 MW CCPP (Summit) | CCGT |  | Bibiyana_400kV | 341
| Bibiyana-III 400 MW CCPP | CCGT |  | Bibiyana_400kV | 400
| Bibiyana South 400 MW |  |  | Bibiyana_400kV | 383
Khulna | Bheramara GTPP Unit-3 |  |  | Bheramara_132kV | 16
| Faridpur 50 MW Peaking PP |  |  | Faridpur_132kV | 54
| Khulna 225 MW CCPP | CCGT |  | KhulnaCentral_132kV | 230
| Gopalganj 100 MW Peaking PP |  |  | Gopalganj_132kV | 109
| Bheramara 410 MW CCPP | CCGT |  | Bheramara_132kV | 410
| Rupsha 105 MW PP (Orion rupsha) |  |  | LabancharaPP_132kV | 105
| Madhumati 100 MW PP |  |  | Gopalganj_132kV | 105
| Mongla Orion 100 MW Solar PP |  |  | Mongla_132kV | 100
| Khulna 330 MW CCPP | CCGT |  | Goalpara_132kV | 336
| Rampal 1320 MW (BIFPCL) |  |  | Rampal_400kV | 1234.2
Barishal | Patuakhali 1320 MW (RNPL) |  |  | RNPL_400kV | 1244
| Barisal 110 MW PP (Summit ) |  |  | Barishal_132kV | 110
| Bhola 33 MW PP (Venture) |  |  | Borhanuddin_230kV | 11.04
| Bhola 225 MW CCPP |  |  | Borhanuddin_230kV | 194
| Payra 1320 MW |  |  | PayraPP_400kV | 1244
| Bhola Nutan Biddut BD LTD |  |  | Borhanuddin_230kV | 220
| United Payra Power Ltd. |  |  | Patuakhali_132kV | 150 |  | 2
| Barisal 307 MW |  |  | Barishal307MWPP_400kV | 307
| Barisal 1 MW Solar Plant |  |  | Barishal_132kV | 1
Rajshahi | Pabna 64 MW Solar Plant |  |  | Pabna64MWSolarPP_132kV | 64.55
| Baghabari 71 MW GTPP |  |  | Baghabari_132kV | 70
| Baghabari 100 MW GTPP |  |  | Baghabari_132kV | 100
| Baghabari 50 MW Peaking PP |  |  | Baghabari_132kV | 52
| Bera 70 MW Peaking PP |  |  | BeraPP_132kV | 71
| Katakhali 50 MW Peaking PP |  |  | Rajshahi_132kV | 50
| Sirajganj 225MW CCPP Unit-1 | CCGT |  | SirajganjSouthWest_230kV | 214
| Sirajganj 225MW CCPP Unit-2 | CCGT |  | SirajganjSouthWest_230kV | 220
| Sirajganj 225MW CCPP Unit-3 | CCGT |  | SirajganjSouthWest_230kV | 220
| Sirajganj 400 MW CCPP Unit-4 | CCGT |  | SirajganjSouthWest_230kV | 413.792
| Santahar 50 MW Peaking PP |  |  | Naogaon_132kV | 50
| Natore 52 MW PP (Rajlanka) |  |  | Natore_132kV | 52.2
| Chapainawabganj 100 MW Peaking PP |  |  | Amnura_132kV | 104
| Bagura 113 MW PP (Confidence)-2 |  |  | BoguraSouth_132kV | 113
| Bagura 113 MW PP (Confidence)-1 |  |  | BoguraSouth_132kV | 113
| Sirajganj 6.55 MW Solar |  |  | Sirajganj_132kV | 6.09
| Sirajganj 68 MW Solar Park |  |  | Sirajganj_132kV | 68
| Pabna Solar 100 MW |  |  | DynamicSunSolarPP_132kV | 100
| Sirajganj 2 MW Wind Power Plant |  |  | Sirajganj_132kV | 2
Rangpur | Saidpur 150 MW Simple Cycle Power Plant |  |  | Saidpur_132kV | 162.443
| Barapukuria TPP Unit-1 & 2 |  |  | Barapukuria_230kV | 170
| Barapukuria 275 MW TPP Unit-3 |  |  | Barapukuria_230kV | 274
| Rangpur 20 MW GTPP |  |  | Rangpur_132kV | 20
| Saidpur 20 MW GTPP |  |  | Saidpur_132kV | 20
| Rangpur 113 MW PP (Confidence) |  |  | ConfidencePP_132kV | 113
| Sympa Solar Power 8 MW |  |  | Panchagarh_132kV | 8
| Energypac Power Venture Thakurgaon Ltd. |  |  | Thakurgaon_132kV | 115
| Intraco Solar 30 MW |  |  | Lalmonirhat_132kV | 30
| Teesta Solar Limited |  |  | TeestaSolar_132kV | 200

## ShuntCapBank
Row 3 contains the names of relevant pypsa variables
CapBank Name | Bus | Rated MVar | Rated kV | Shunt Susceptance
name | bus |  |  | b
PanchagarhCapBank |  | 22.5 | 132 | 0.00074555
JaldhakaCapBank |  | 22.5 | 132 | 0.00074555
IshwardiCapBank |  | 45 | 132 | 0.0014911
JashoreCapBank |  | 45 | 132 | 0.0014911
KhulnaSouthCapBank |  | 45 | 132 | 0.0014911
BarishalCapBank |  | 22.5 | 132 | 0.00074555
AminbazarCapBank1 |  | 45 | 132 | 0.0014911
AminbazarCapBank2 |  | 45 | 132 | 0.0014911
RampuraCapBank1 |  | 45 | 132 | 0.0014911
RampuraCapBank2 |  | 45 | 132 | 0.0014911
HathazariCapBank |  | 45 | 132 | 0.0014911