## lines
Row 3 contains the names of relevant pypsa variables
Line Name | Start Bus | End Bus | Length(km) | Conductor | Line Resistance (Ohm) | Line Inductive Reactance (Ohm) | Line Shunt Susceptance (Siemens) | Line Nominal Capacity (MVA)
name | bus0 | bus1 |  |  | r | x | b | s_nom
BheramaraHVDC1_400kV_DCtoBangladesh Border1_400kV_DC_Line1 | BheramaraHVDC1_400kV_DC | BangladeshBorder1_400kV_DC | 27.35 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
BheramaraHVDC1_400kV_DCtoBangladesh Border1_400kV_DC_Line2 | BheramaraHVDC1_400kV_DC | BangladeshBorder1_400kV_DC | 27.35 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
Aminbazar_400kVtoMeghnaghat_400kV_Line1 | Aminbazar_400kV | Meghnaghat_400kV | 55 | Quad Egret | 0.02755 | 0.081959 | 2.65e-05 | 400
Aminbazar_400kVtoMeghnaghat_400kV_Line2 | Aminbazar_400kV | Meghnaghat_400kV | 55 | Quad Egret | 0.02755 | 0.081959 | 2.65e-05 | 400
SuryamaninagarRecvBus_132kVtoCumillaSouth_132kV_Line1 | SuryamaninagarRecvBus_132kV | CumillaSouth_132kV | 47 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
SuryamaninagarRecvBus_132kVtoCumillaSouth_132kV_Line2 | SuryamaninagarRecvBus_132kV | CumillaSouth_132kV | 47 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
Bibiyana_400kVtoKaliakoir_400kV_Line1 | Bibiyana_400kV | Kaliakoir_400kV | 169.5 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
Bibiyana_400kVtoKaliakoir_400kV_Line2 | Bibiyana_400kV | Kaliakoir_400kV | 169.5 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
AshuganjNorth_400kVtoBhulta_400kV_Line1 | AshuganjNorth_400kV | Bhulta_400kV | 69 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
AshuganjNorth_400kVtoBhulta_400kV_Line2 | AshuganjNorth_400kV | Bhulta_400kV | 69 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
Payra_400kVtoGopalganjNorth_400kV_Line1 | Payra_400kV | GopalganjNorth_400kV | 163.55 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
Payra_400kVtoGopalganjNorth_400kV_Line2 | Payra_400kV | GopalganjNorth_400kV | 163.55 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
BSRM_230kVtoMirsarai_230kV_Line1 | BSRM_230kV | Mirsarai_230kV | 16.5 | Twin Finch | 0.027187 | 0.12927 | 1.43e-05 | 400
BSRM_230kVtoMirsarai_230kV_Line2 | BSRM_230kV | Mirsarai_230kV | 16.5 | Twin Finch | 0.027187 | 0.12927 | 1.43e-05 | 400
BheramaraHVDC2_400kV_DCtoBangladeshBorder2_400kV_DC_Line1 | BheramaraHVDC2_400kV_DC | BangladeshBorder2_400kV_DC | 28 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
BheramaraHVDC2_400kV_DCtoBangladeshBorder2_400kV_DC_Line2 | BheramaraHVDC2_400kV_DC | BangladeshBorder2_400kV_DC | 28 | Twin Finch | 0.031985 | 0.12927 | 1.43e-05 | 400
PayraPP_400kVtoPayra_400kV_Line1 | PayraPP_400kV | Payra_400kV | 1.2 | Quad Finch | 0.06397 | 0.2362 | 7.17e-06 | 400
PayraPP_400kVtoPayra_400kV_Line2 | PayraPP_400kV | Payra_400kV | 1.2 | Quad Finch | 0.06397 | 0.2362 | 7.17e-06 | 400
Banskhali_400kVtoMadunaghatNew_400kV_Line1 | Banskhali_400kV | MadunaghatNew_400kV | 55.5 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
Banskhali_400kVtoMadunaghatNew_400kV_Line2 | Banskhali_400kV | MadunaghatNew_400kV | 55.5 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
AdaniPPRecvBus_400kVtoRahanpur_400kV_Line1 | AdaniPPRecvBus_400kV | Rahanpur_400kV | 134 | Twin Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
AdaniPPRecvBus_400kVtoRahanpur_400kV_Line2 | AdaniPPRecvBus_400kV | Rahanpur_400kV | 134 | Twin Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
Rampal_400kVtoGopalganjNorth_400kV_Line1 | Rampal_400kV | GopalganjNorth_400kV | 96.7 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
Rampal_400kVtoGopalganjNorth_400kV_Line2 | Rampal_400kV | GopalganjNorth_400kV | 96.7 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
GopalganjNorth_400kVtoAminbazar_400kV_Line1 | GopalganjNorth_400kV | Aminbazar_400kV | 75.3 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
GopalganjNorth_400kVtoAminbazar_400kV_Line2 | GopalganjNorth_400kV | Aminbazar_400kV | 75.3 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
BoguraWest_400kVtoRahanpur_400kV_Line1 | BoguraWest_400kV | Rahanpur_400kV | 105 | Twin Finch | 0.027187 | 0.12927 | 1.43e-05 | 400
BoguraWest_400kVtoRahanpur_400kV_Line2 | BoguraWest_400kV | Rahanpur_400kV | 105 | Twin Finch | 0.027187 | 0.12927 | 1.43e-05 | 400
Barishal307MWPP_400kVtoPayraPP_400kV_Line1 | Barishal307MWPP_400kV | PayraPP_400kV | 27.8 | Quad Finch | 0.06397 | 0.2362 | 7.17e-06 | 400
Barishal307MWPP_400kVtoPayraPP_400kV_Line2 | Barishal307MWPP_400kV | PayraPP_400kV | 27.8 | Quad Finch | 0.06397 | 0.2362 | 7.17e-06 | 400
Matarbari_400kVtoBanskhali_400kV_Line1 | Matarbari_400kV | Banskhali_400kV | 38 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
Matarbari_4002kVtoBanskhali_400kV_Line2 | Matarbari_400kV | Banskhali_400kV | 38 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
MadunaghatNew_400kVtoKorerhat_400kV_Line1 | MadunaghatNew_400kV | Korerhat_400kV | 66 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
MadunaghatNew_400kVtoKorerhat_400kV_Line2 | MadunaghatNew_400kV | Korerhat_400kV | 66 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
Meghnaghat_400kVtoKorerhat_400kV_Line1 | Meghnaghat_400kV | Korerhat_400kV | 151 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
Meghnaghat_400kVtoKorerhat_400kV_Line2 | Meghnaghat_400kV | Korerhat_400kV | 151 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
RNPP_400kVtoBoguraWest_400kV_Line1 | RNPP_400kV | BoguraWest_400kV | 90 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
BoguraWest_400kVtoBarapukuriaNorth_400kV_Line1 | BoguraWest_400kV | BarapukuriaNorth_400kV | 112 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
BoguraWest_400kVtoBarapukuriaNorth_400kV_Line2 | BoguraWest_400kV | BarapukuriaNorth_400kV | 112 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
PayraPP_400kVtoAmtali_400kV_Line1 | PayraPP_400kV | Amtali_400kV | 17 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
PayraPP_400kVtoAmtali_400kV_Line2 | PayraPP_400kV | Amtali_400kV | 17 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
GopalganjNorth_400kVtoAmtali_400kV_Line1 | GopalganjNorth_400kV | Amtali_400kV | 147 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
GopalganjNorth_400kVtoAmtali_400kV_Line2 | GopalganjNorth_400kV | Amtali_400kV | 147 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
Amtali_400kVtoRNPL_400kV_Line1 | Amtali_400kV | RNPL_400kV | 9.9 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
Amtali_400kVtoRNPL_400kV_Line2 | Amtali_400kV | RNPL_400kV | 9.9 | Quad Finch | 0.015992 | 0.075809 | 2.87e-05 | 400
Bogura_400kVtoKaliakoir_400kV_Line1 | Bogura_400kV | Kaliakoir_400kV | 73 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
Bogura_400kVtoKaliakoir_400kV_Line2 | Bogura_400kV | Kaliakoir_400kV | 73 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
Aminbazar_400kVtoKaliakoir_400kV_Line1 | Aminbazar_400kV | Kaliakoir_400kV | 51 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
RNPP_400kVtoGopalganjNorth_400kV_Line1 | RNPP_400kV | GopalganjNorth_400kV | 156 | Quad Finch | 0.013593 | 0.075809 | 2.87e-05 | 400
Ghorashal_230kVtoIshwardi_230kV_Line1 | Ghorashal_230kV | Ishwardi_230kV | 175 | Mallard | 0.08831 | 0.2441 | 6.87e-06 | 230
Ghorashal_230kVtoIshwardi_230kV_Line2 | Ghorashal_230kV | Ishwardi_230kV | 175 | Mallard | 0.08831 | 0.2441 | 6.87e-06 | 230
Tongi_230kVtoGhorashal_230kV_Line1 | Tongi_230kV | Ghorashal_230kV | 27 | Mallard | 0.070648 | 0.2441 | 6.87e-06 | 230
Tongi_230kVtoGhorashal_230kV_Line2 | Tongi_230kV | Ghorashal_230kV | 27 | Mallard | 0.070648 | 0.2441 | 6.87e-06 | 230
Ghorashal_230kVtoAshuganj_230kV_Line1 | Ghorashal_230kV | Ashuganj_230kV | 44 | Mallard | 0.08831 | 0.2441 | 6.87e-06 | 230
Ghorashal_230kVtoAshuganj_230kV_Line2 | Ghorashal_230kV | Ashuganj_230kV | 44 | Mallard | 0.08831 | 0.2441 | 6.87e-06 | 230
Raozan_230kVtoHathazari_230kV_Line1 | Raozan_230kV | Hathazari_230kV | 22.5 | Twin 300 sqmm | 0.1101 | 0.2559 | 6.57e-06 | 230
Raozan_230kVtoHathazari_230kV_Line2 | Raozan_230kV | Hathazari_230kV | 22.5 | Twin 300 sqmm | 0.1101 | 0.2559 | 6.57e-06 | 230
Ashuganj_230kVtoCumillaNorth_230kV_Line1 | Ashuganj_230kV | CumillaNorth_230kV | 79 | Finch | 0.06397 | 0.2362 | 7.17e-06 | 230
Ashuganj_230kVtoCumillaNorth_230kV_Line2 | Ashuganj_230kV | CumillaNorth_230kV | 79 | Finch | 0.06397 | 0.2362 | 7.17e-06 | 230
Ghorashal_230kVtoBhulta_230kV_Line1 | Ghorashal_230kV | Bhulta_230kV | 50 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Ghorashal_230kVtoBhulta_230kV_Line2 | Ghorashal_230kV | Bhulta_230kV | 50 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Bhulta_230kVtoRampura_230kV_Line1 | Bhulta_230kV | Rampura_230kV | 20 | Twin Mallard
Bhulta_230kVtoRampura_230kV_Line2 | Bhulta_230kV | Rampura_230kV | 20 | Twin Mallard
Haripur_230kVtoBhulta_230kV_Line1 | Haripur_230kV | Bhulta_230kV | 22 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Haripur_230kVtoBhulta_230kV_Line2 | Haripur_230kV | Bhulta_230kV | 22 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Bhulta_230kVtoRampura_230kV_Line3 | Bhulta_230kV | Rampura_230kV | 20 | Twin Mallard
Bhulta_230kVtoRampura_230kV_Line4 | Bhulta_230kV | Rampura_230kV | 20 | Twin Mallard
Haripur_230kVtoMeghnaghat_230kV_Line1 | Haripur_230kV | Meghnaghat_230kV | 12.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Haripur_230kVtoMeghnaghat_230kV_Line2 | Haripur_230kV | Meghnaghat_230kV | 12.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Meghnaghat_230kVtoShyampur_230kV_Line1 | Meghnaghat_230kV | Shyampur_230kV | 12.25 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Meghnaghat_230kVtoShyampur_230kV_Line2 | Meghnaghat_230kV | Shyampur_230kV | 12.25 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Shyampur_230kVtoHasnabad_230kV_Line1 | Shyampur_230kV | Hasnabad_230kV | 12.25 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Shyampur_230kVtoHasnabad_230kV_Line2 | Shyampur_230kV | Hasnabad_230kV | 12.25 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
CumillaNorth_230kVtoFeniNorth_230kV_Line1 | CumillaNorth_230kV | FeniNorth_230kV | 70 | Finch | 0.06397 | 0.2362 | 7.17e-06 | 230
CumillaNorth_230kVtoFeniNorth_230kV_Line2 | CumillaNorth_230kV | FeniNorth_230kV | 70 | Finch | 0.06397 | 0.2362 | 7.17e-06 | 230
FeniNorth_230kVtoBSRM_230kV_Line1 | FeniNorth_230kV | BSRM_230kV | 26 | Finch
FeniNorth_230kVtoBSRM_230kV_Line2 | FeniNorth_230kV | BSRM_230kV | 26 | Finch
BSRM_230kVtoGPH_230kV_Line1 | BSRM_230kV | GPH_230kV | 40 | Finch
BSRM_230kVtoGPH_230kV_Line2 | BSRM_230kV | GPH_230kV | 40 | Finch
GPH_230kVtoAKSPL_230kV_Line1 | GPH_230kV | AKSPL_230kV | 13 | Finch
GPH_230kVtoAKSPL_230kV_Line2 | GPH_230kV | AKSPL_230kV | 13 | Finch
AKSPL_230kVtoHathazari_230kV_Line1 | AKSPL_230kV | Hathazari_230kV | 9 | Finch
AKSPL_230kVtoHathazari_230kV_Line2 | AKSPL_230kV | Hathazari_230kV | 9 | Finch
AESHaripur_230kVtoHaripur_230kV_Line1 | AESHaripur_230kV | Haripur_230kV | 2.4 | Finch | 0.06397 | 0.2362 | 7.17e-06 | 230
AESHaripur_230kVtoHaripur_230kV_Line2 | AESHaripur_230kV | Haripur_230kV | 2.4 | Finch | 0.06397 | 0.2362 | 7.17e-06 | 230
CumillaNorth_230kVtoMeghnaghat_230kV_Line1 | CumillaNorth_230kV | Meghnaghat_230kV | 58 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
CumillaNorth_230kVtoMeghnaghat_230kV_Line2 | CumillaNorth_230kV | Meghnaghat_230kV | 58 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Tongi_230kVtoKaliakoir_230kV_Line1 | Tongi_230kV | Kaliakoir_230kV | 25.2 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Tongi_230kVtoKaliakoir_230kV_Line2 | Tongi_230kV | Kaliakoir_230kV | 25.2 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Kaliakoir_230kVtoAminbazar_230kV_Line1 | Kaliakoir_230kV | Aminbazar_230kV | 32 | Twin AAAC
Kaliakoir_230kVtoAminbazar_230kV_Line2 | Kaliakoir_230kV | Aminbazar_230kV | 32 | Twin AAAC
Aminbazar_230kVtoKeraniganj_230kV_Line1 | Aminbazar_230kV | Keraniganj_230kV | 10.75 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Aminbazar_230kVtoKeraniganj_230kV_Line2 | Aminbazar_230kV | Keraniganj_230kV | 10.75 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Hasnabad_230kVtoKeraniganj_230kV_Line1 | Hasnabad_230kV | Keraniganj_230kV | 10.75 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Hasnabad_230kVtoKeraniganj_230kV_Line2 | Hasnabad_230kV | Keraniganj_230kV | 10.75 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Ashuganj_230kVtoSripur_230kV_Line1 | Ashuganj_230kV | Sripur_230kV | 75 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Ashuganj_230kVtoSripur_230kV_Line2 | Ashuganj_230kV | Sripur_230kV | 75 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Sripur_230kVtoSirajganjSouthWest_230kV_Line1 | Sripur_230kV | SirajganjSouthWest_230kV | 69 | Twin AAAC
Sripur_230kVtoSirajganjSouthWest_230kV_Line2 | Sripur_230kV | SirajganjSouthWest_230kV | 69 | Twin AAAC
KhulnaSouth_230kVtoJhenaidahSouth_230kV_Line1 | KhulnaSouth_230kV | JhenaidahSouth_230kV | 96 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
KhulnaSouth_230kVtoJhenaidahSouth_230kV_Line2 | KhulnaSouth_230kV | JhenaidahSouth_230kV | 96 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
JhenaidahSouth_230kVtoBheramaraHVDC_230kV_Line1 | JhenaidahSouth_230kV | BheramaraHVDC_230kV | 80.5 | Twin AAAC
JhenaidahSouth_230kVtoBheramaraHVDC_230kV_Line2 | JhenaidahSouth_230kV | BheramaraHVDC_230kV | 80.5 | Twin AAAC
BoguraWest_230kVtoBarapukuria_230kV_Line1 | BoguraWest_230kV | Barapukuria_230kV | 106 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
BoguraWest_230kVtoBarapukuria_230kV_Line2 | BoguraWest_230kV | Barapukuria_230kV | 106 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
BoguraSouth_230kVtoBoguraWest_230kV_Line1 | BoguraSouth_230kV | BoguraWest_230kV | 11 | Twin AAAC
BoguraSouth_230kVtoBoguraWest_230kV_Line2 | BoguraSouth_230kV | BoguraWest_230kV | 11 | Twin AAAC
BoguraSouth_230kVtoBoguraWest_230kV_Line3 | BoguraSouth_230kV | BoguraWest_230kV | 11 | Twin AAAC
BoguraSouth_230kVtoBoguraWest_230kV_Line4 | BoguraSouth_230kV | BoguraWest_230kV | 11 | Twin AAAC
SirajganjSouthWest_230kVtoBoguraSouth_230kV_Line1 | SirajganjSouthWest_230kV | BoguraSouth_230kV | 72.5 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
SirajganjSouthWest_230kVtoBoguraSouth_230kV_Line2 | SirajganjSouthWest_230kV | BoguraSouth_230kV | 72.5 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Ishwardi_230kVtoBaghabari_230kV_Line1 | Ishwardi_230kV | Baghabari_230kV | 55 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Ishwardi_230kVtoBaghabari_230kV_Line2 | Ishwardi_230kV | Baghabari_230kV | 55 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Baghabari_230kVtoSirajganjSouthWest_230kV_Line1 | Baghabari_230kV | SirajganjSouthWest_230kV | 38 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Baghabari_230kVtoSirajganjSouthWest_230kV_Line2 | Baghabari_230kV | SirajganjSouthWest_230kV | 38 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Fenchuganj_230kVtoBibiyana_230kV_Line1 | Fenchuganj_230kV | Bibiyana_230kV | 33.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Fenchuganj_230kVtoBibiyana_230kV_Line2 | Fenchuganj_230kV | Bibiyana_230kV | 33.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Bibiyana_230kVtoShahjibazar_230kV_Line1 | Bibiyana_230kV | Shahjibazar_230kV | 95 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Bibiyana_230kVtoShahjibazar_230kV_Line2 | Bibiyana_230kV | Shahjibazar_230kV | 95 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Shahjibazar_230kVtoCumillaNorth_230kV_Line1 | Shahjibazar_230kV | CumillaNorth_230kV | 58.5 | Twin Mallard
Shahjibazar_230kVtoCumillaNorth_230kV_Line2 | Shahjibazar_230kV | CumillaNorth_230kV | 58.5 | Twin Mallard
Aminbazar_230kVtoAgargaon_230kV_Line1 | Aminbazar_230kV | Agargaon_230kV | 7.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Aminbazar_230kVtoAgargaon_230kV_Line2 | Aminbazar_230kV | Agargaon_230kV | 7.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Siddhirganj_230kVtoManiknagar_230kV_Line1 | Siddhirganj_230kV | Maniknagar_230kV | 11 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Siddhirganj_230kVtoManiknagar_230kV_Line2 | Siddhirganj_230kV | Maniknagar_230kV | 11 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
BarishalNorth_230kVtoBorhanuddin_230kV_Line1 | BarishalNorth_230kV | Borhanuddin_230kV | 62.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
BarishalNorth_230kVtoBorhanuddin_230kV_Line2 | BarishalNorth_230kV | Borhanuddin_230kV | 62.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
BheramaraHVDC_230kVtoBheramara_230kV_Line1 | BheramaraHVDC_230kV | Bheramara_230kV | 6 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
BheramaraHVDC_230kVtoBheramara_230kV_Line2 | BheramaraHVDC_230kV | Bheramara_230kV | 6 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 230
Haripur_230kVtoSiddhirganj_230kV_Line1 | Haripur_230kV | Siddhirganj_230kV | 1.65 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Haripur_230kVtoSiddhirganj_230kV_Line2 | Haripur_230kV | Siddhirganj_230kV | 1.65 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
BheramaraHVDC_230kVtoIshwardi_230kV_Line1 | BheramaraHVDC_230kV | Ishwardi_230kV | 12.8 | Quad Mallard | 0.022077 | 0.078468 | 2.75e-05 | 230
BheramaraHVDC_230kVtoIshwardi_230kV_Line2 | BheramaraHVDC_230kV | Ishwardi_230kV | 12.8 | Quad Mallard | 0.022077 | 0.078468 | 2.75e-05 | 230
Sikalbaha_230kVtoAnwara_230kV_Line1 | Sikalbaha_230kV | Anwara_230kV | 17.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Sikalbaha_230kVtoAnwara_230kV_Line2 | Sikalbaha_230kV | Anwara_230kV | 17.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Patuakhali_230kVtoPayra_230kV_Line1 | Patuakhali_230kV | Payra_230kV | 46.5 | Twin Mallard | 0.035324 | 0.13368 | 1.37e-05 | 230
Patuakhali_230kVtoPayra_230kV_Line2 | Patuakhali_230kV | Payra_230kV | 46.5 | Twin Mallard | 0.035324 | 0.13368 | 1.37e-05 | 230
RajshahiNorth_230kVtoBheramaraHVDC_230kV_Line1 | RajshahiNorth_230kV | BheramaraHVDC_230kV | 66.2 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
RajshahiNorth_230kVtoBheramaraHVDC_230kV_Line2 | RajshahiNorth_230kV | BheramaraHVDC_230kV | 66.2 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
MadunaghatNew_230kVtoHathazari_230kV_Line1 | MadunaghatNew_230kV | Hathazari_230kV | 28.35 | Quad Mallard | 0.022077 | 0.078468 | 2.75e-05 | 230
MadunaghatNew_230kVttoHathazari_230kV_Line2 | MadunaghatNew_230kV | Hathazari_230kV | 28.35 | Quad Mallard | 0.022077 | 0.078468 | 2.75e-05 | 230
Rampal_230kVtoKhulnaSouth_230kV_Line1 | Rampal_230kV | KhulnaSouth_230kV | 24 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Rampal_230kVtoKhulnaSouth_230kV_Line2 | Rampal_230kV | KhulnaSouth_230kV | 24 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
BarishalNorth_230kVtoGopalganjNorth_230kV_Line1 | BarishalNorth_230kV | GopalganjNorth_230kV | 75 | Twin Mallard | 0.035324 | 0.13368 | 1.37e-05 | 230
BarishalNorth_230kVtoGopalganjNorth_230kV_Line2 | BarishalNorth_230kV | GopalganjNorth_230kV | 75 | Twin Mallard | 0.035324 | 0.13368 | 1.37e-05 | 230
GopalganjNorth_230kVtoFaridpur_230kV_Line1 | GopalganjNorth_230kV | Faridpur_230kV | 49 | Twin Mallard | 0.035324 | 0.13368 | 1.37e-05 | 230
GopalganjNorth_230kVtoFaridpur_230kV_Line2 | GopalganjNorth_230kV | Faridpur_230kV | 49 | Twin Mallard | 0.035324 | 0.13368 | 1.37e-05 | 230
MadunaghatNew_230kVtoSikalbaha_230kV_Line1 | MadunaghatNew_230kV | Sikalbaha_230kV | 11.7 | Quad Mallard | 0.022077 | 0.078468 | 2.75e-05 | 230
MadunaghatNew_230kVtoSikalbaha_230kV_Line2 | MadunaghatNew_230kV | Sikalbaha_230kV | 11.7 | Quad Mallard | 0.022077 | 0.078468 | 2.75e-05 | 230
MadunaghatNew_230kVtoMadunaghat_230kV_Line1 | MadunaghatNew_230kV | Madunaghat_230kV | 7 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
MadunaghatNew_230kVtoMadunaghat_230kV_Line2 | MadunaghatNew_230kV | Madunaghat_230kV | 7 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
RNPP_230kVtoBaghabari_230kV_Line1 | RNPP_230kV | Baghabari_230kV | 65.5 | Twin Mallard | 0.035324 | 0.13368 | 1.37e-05 | 230
RNPP_230kVtoBaghabari_230kV_Line2 | RNPP_230kV | Baghabari_230kV | 65.5 | Twin Mallard | 0.035324 | 0.13368 | 1.37e-05 | 230
Khulna330MW_230kVtoKhulnaSouth_230kV_Line1 | Khulna330MW_230kV | KhulnaSouth_230kV | 14 | Twin Mallard | 0.06397 | 0.2362 | 7.17e-06 | 230
Sonagazi_230kVtoMirsarai_230kV_Line1 | Sonagazi_230kV | Mirsarai_230kV | 13.3 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Korerhat_230kVtoChowmuhani_230kV_Line1 | Korerhat_230kV | Chowmuhani_230kV | 54 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Korerhat_230kVtoChowmuhani_230kV_Line2 | Korerhat_230kV | Chowmuhani_230kV | 54 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Korerhat_230kVtoChowmuhani_230kV_Line3 | Korerhat_230kV | Chowmuhani_230kV | 54 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Korerhat_230kVtoChowmuhani_230kV_Line4 | Korerhat_230kV | Chowmuhani_230kV | 54 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Chowmuhani_230kVtoKachua_230kV_Line1 | Chowmuhani_230kV | Kachua_230kV | 50.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Chowmuhani_230kVtoKachua_230kV_Line2 | Chowmuhani_230kV | Kachua_230kV | 50.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Chowmuhani_230kVtoKachua_230kV_Line3 | Chowmuhani_230kV | Kachua_230kV | 50.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Chowmuhani_230kVtoKachua_230kV_Line4 | Chowmuhani_230kV | Kachua_230kV | 50.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Chowmuhani_230kVtoMaijdee_230kV_Line1 | Chowmuhani_230kV | Maijdee_230kV | 20.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Chowmuhani_230kVtoMaijdee_230kV_Line2 | Chowmuhani_230kV | Maijdee_230kV | 20.5 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Barapukuria_230kVtoPurbasadipur_230kV_Line1 | Barapukuria_230kV | Purbasadipur_230kV | 38.7 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Barapukuria_230kVtoPurbasadipur_230kV_Line2 | Barapukuria_230kV | Purbasadipur_230kV | 38.7 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Kachua_230kVtoGazaria_230kV_Line1 | Kachua_230kV | Gazaria_230kV | 49 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Kachua_230kVtoGazaria_230kV_Line2 | Kachua_230kV | Gazaria_230kV | 49 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Kachua_230kVtoGazaria_230kV_Line3 | Kachua_230kV | Gazaria_230kV | 49 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
Kachua_230kVtoGazaria_230kV_Line4 | Kachua_230kV | Gazaria_230kV | 49 | Twin Mallard | 0.044155 | 0.13368 | 1.37e-05 | 230
GhorashalSouthWest_230kVtoGhorashal_230kV_Line1 | GhorashalSouthWest_230kV | Ghorashal_230kV | 1.1 | XLPE 2000 sq mm | 0.015 | 0.12 | 2e-05 | 230
GhorashalSouthWest_230kVtoGhorashal_230kV_Line2 | GhorashalSouthWest_230kV | Ghorashal_230kV | 1.1 | XLPE 2000 sq mm | 0.015 | 0.12 | 2e-05 | 230
GhorashalSouthWest_230kVtoGhorashal_230kV_Line3 | GhorashalSouthWest_230kV | Ghorashal_230kV | 1.1 | XLPE 2000 sq mm | 0.015 | 0.12 | 2e-05 | 230
Shahjibazar_132kVtoBrahmanbaria_132kV_Line1 | Shahjibazar_132kV | Brahmanbaria_132kV | 57 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Shahjibazar_132kVtoBrahmanbaria_132kV_Line2 | Shahjibazar_132kV | Brahmanbaria_132kV | 57 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Brahmanbaria_132kVtoAshuganj_132kV_Line1 | Brahmanbaria_132kV | Ashuganj_132kV | 16.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Brahmanbaria_132kVtoAshuganj_132kV_Line2 | Brahmanbaria_132kV | Ashuganj_132kV | 16.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ashuganj_132kVtoGhorashal_132kV_Line1 | Ashuganj_132kV | Ghorashal_132kV | 45.5 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Ashuganj_132kVtoGhorashal_132kV_Line2 | Ashuganj_132kV | Ghorashal_132kV | 45.5 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Ghorashal_132kVtoNarsingdi_132kV_Line1 | Ghorashal_132kV | Narsingdi_132kV | 13.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ghorashal_132kVtoNarsingdi_132kV_Line2 | Ghorashal_132kV | Narsingdi_132kV | 13.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Narsingdi_132kVtoBhulta_132kV_Line1 | Narsingdi_132kV | Bhulta_132kV | 19 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Narsingdi_132kVtoBhulta_132kV_Line2 | Narsingdi_132kV | Bhulta_132kV | 19 | Grosbeak
Bhulta_132kVtoHaripur_132kV_Line1 | Bhulta_132kV | Haripur_132kV | 15 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Bhulta_132kVtoHaripur_132kV_Line2 | Bhulta_132kV | Haripur_132kV | 15 | Grosbeak
Shahjibazar_132kVtoSrimangal_132kV_Line1 | Shahjibazar_132kV | Srimangal_132kV | 36 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Shahjibazar_132kVtoSrimangal_132kV_Line2 | Shahjibazar_132kV | Srimangal_132kV | 36 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Srimangal_132kVtoFenchuganj_132kV_Line1 | Srimangal_132kV | Fenchuganj_132kV | 49 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Srimangal_132kVtoFenchuganj_132kV_Line2 | Srimangal_132kV | Fenchuganj_132kV | 49 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
FenchuganjPS_132kVtoFenchuganj_132kV_Line1 | FenchuganjPS_132kV | Fenchuganj_132kV | 3.75 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
FenchuganjPS_132kVtoFenchuganj_132kV_Line2 | FenchuganjPS_132kV | Fenchuganj_132kV | 3.75 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
FenchuganjPS_132kVtoFenchuganj_132kV_Line3 | FenchuganjPS_132kV | Fenchuganj_132kV | 3.75 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
FenchuganjPS_132kVtoFenchuganj_132kV_Line4 | FenchuganjPS_132kV | Fenchuganj_132kV | 3.75 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
FenchuganjPS_132kVtoSylhetSouth_132kV_Line1 | SylhetSouth_132kV | Fenchuganj_132kV | 5 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
SylhetSouth_132kVtoFenchuganj_132kV_Line1 | SylhetSouth_132kV | Fenchuganj_132kV | 25 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Sylhet_132kVtoSylhetSouth_132kV_Line1 | Sylhet_132kV | SylhetSouth_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sylhet_132kVtoSylhetSouth_132kV_Line2 | Sylhet_132kV | SylhetSouth_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sylhet_132kVtoChhatak_132kV_Line1 | Sylhet_132kV | Chhatak_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sylhet_132kVtoChhatak_132kV_Line2 | Sylhet_132kV | Chhatak_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kaptai_132kVtoHathazari_132kV_Line1 | Kaptai_132kV | Hathazari_132kV | 45 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kaptai_132kVtoHathazari_132kV_Line2 | Kaptai_132kV | Hathazari_132kV | 45 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Hathazari_132kVtoBaroirhat_132kV_Line1 | Hathazari_132kV | Baroirhat_132kV | 63.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Hathazari_132kVtoBaroirhat_132kV_Line2 | Hathazari_132kV | Baroirhat_132kV | 63.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Feni_132kVtoCumillaNorth_132kV_Line1 | Feni_132kV | CumillaNorth_132kV | 66 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Feni_132kVtoCumillaNorth_132kV_Line2 | Feni_132kV | CumillaNorth_132kV | 66 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaNorth_132kVtoMuradnagar_132kV_Line1 | CumillaNorth_132kV | Muradnagar_132kV | 29 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaNorth_132kVtoMuradnagar_132kV_Line2 | CumillaNorth_132kV | Muradnagar_132kV | 29 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Muradnagar_132kVtoDaudkandi_132kV_Line1 | Muradnagar_132kV | Daudkandi_132kV | 26 | Grosbeak
Muradnagar_132kVtoDaudkandi_132kV_Line2 | Muradnagar_132kV | Daudkandi_132kV | 26 | Grosbeak
Daudkandi_132kVtoSonargaon_132kV_Line1 | Daudkandi_132kV | Sonargaon_132kV | 61.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Daudkandi_132kVtoSonargaon_132kV_Line2 | Daudkandi_132kV | Sonargaon_132kV | 61.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sonargaon_132kVtoHaripur_132kV_Line1 | Sonargaon_132kV | Haripur_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sonargaon_132kVtoHaripur_132kV_Line2 | Sonargaon_132kV | Haripur_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Haripur_132kVtoSiddhirganj_132kV_Line1 | Haripur_132kV | Siddhirganj_132kV | 2.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Haripur_132kVtoSiddhirganj_132kV_Line2 | Haripur_132kV | Siddhirganj_132kV | 2.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaNorth_132kVtoKachua_132kV_Line1 | CumillaNorth_132kV | Kachua_132kV | 56 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaSouth_132kVtoKachua_132kV_Line1 | CumillaSouth_132kV | Kachua_132kV | 40 | Linnet | 0.1101 | 0.2559 | 6.57e-06 | 132
Kachua_132kVtoChandpur_132kV_Line1 | Kachua_132kV | Chandpur_132kV | 22 | Grosbeak
Kachua_132kVtoChandpur_132kV_Line2 | Kachua_132kV | Chandpur_132kV | 22 | Grosbeak
Ashuganj_132kVtoBajitpur_132kV_Line1 | Ashuganj_132kV | Bajitpur_132kV | 21 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Ashuganj_132kVtoBajitpur_132kV_Line2 | Ashuganj_132kV | Bajitpur_132kV | 21 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Bajitpur_132kVtoKishoreganj_132kV_Line1 | Bajitpur_132kV | Kishoreganj_132kV | 31 | Grosbeak
Bajitpur_132kVtoKishoreganj_132kV_Line2 | Bajitpur_132kV | Kishoreganj_132kV | 31 | Grosbeak
Kishoreganj_132kVtoMymensingh_132kV_Line1 | Kishoreganj_132kV | Mymensingh_132kV | 59 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kishoreganj_132kVtoMymensingh_132kV_Line2 | Kishoreganj_132kV | Mymensingh_132kV | 59 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mymensingh_132kVtoJamalpur_132kV_Line1 | Mymensingh_132kV | Jamalpur_132kV | 55 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Mymensingh_132kVtoJamalpur_132kV_Line2 | Mymensingh_132kV | Jamalpur_132kV | 55 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Madunaghat_132kVtoSikalbaha_132kV_Line1 | Madunaghat_132kV | Sikalbaha_132kV | 17 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madunaghat_132kVtoTKCCL_132kV_Line1 | Madunaghat_132kV | TKCCL_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
TKCCL_132kVtoSikalbaha_132kV_Line1 | TKCCL_132kV | Sikalbaha_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sikalbaha_132kVtoPatiya_132kV_Line1 | Sikalbaha_132kV | Patiya_132kV | 11 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Sikalbaha_132kVtoPatiya_132kV_Line2 | Sikalbaha_132kV | Patiya_132kV | 11 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Patiya_132kVtoDohazari_132kV_Line1 | Patiya_132kV | Dohazari_132kV | 21 | Grosbeak
Patiya_132kVtoDohazari_132kV_Line2 | Patiya_132kV | Dohazari_132kV | 21 | Grosbeak
Sikalbaha_132kVtoJuldah_132kV_Line1 | Sikalbaha_132kV | Juldah_132kV | 8 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Juldah_132kVtoHalishahar_132kV_Line1 | Juldah_132kV | Halishahar_132kV | 8 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Khulshi_132kVtoBaroaulia_132kV_Line1 | Khulshi_132kV | Baroaulia_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Khulshi_132kVtoAKSML_132kV_Line1 | Khulshi_132kV | AKSML_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
AKSML_132kVtoBaroaulia_132kV_Line1 | AKSML_132kV | Baroaulia_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madunaghat_132kVtoSholoshahar_132kV_Line1 | Madunaghat_132kV | Sholoshahar_132kV | 6.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madunaghat_132kVtoSholoshahar_132kV_Line2 | Madunaghat_132kV | Sholoshahar_132kV | 6.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sholoshahar_132kVtoKhulshi_132kV_Line1 | Sholoshahar_132kV | Khulshi_132kV | 6.5 | Grosbeak
Sholoshahar_132kVtoKhulshi_132kV_Line2 | Sholoshahar_132kV | Khulshi_132kV | 6.5 | Grosbeak
Kaptai_132kVtoChandraghona_132kV_Line1 | Kaptai_132kV | Chandraghona_132kV | 11.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kaptai_132kVtoChandraghona_132kV_Line2 | Kaptai_132kV | Chandraghona_132kV | 11.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chandraghona_132kVtoMadunaghat_132kV_Line1 | Chandraghona_132kV | Madunaghat_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chandraghona_132kVtoMadunaghat_132kV_Line2 | Chandraghona_132kV | Madunaghat_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madunaghat_132kVtoHathazari_132kV_Line1 | Madunaghat_132kV | Hathazari_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madunaghat_132kVtoHathazari_132kV_Line2 | Madunaghat_132kV | Hathazari_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Hathazari_132kVtoBaroaulia_132kV_Line1 | Hathazari_132kV | Baroaulia_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Hathazari_132kVtoBaroaulia_132kV_Line2 | Hathazari_132kV | Baroaulia_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Dohazari_132kVtoCox'sBazar_132kV_Line1 | Dohazari_132kV | Cox'sBazar_132kV | 87 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Dohazari_132kVtoMatarbariTConnection_132kV_Line1 | Dohazari_132kV | MatarbariTConnection_132kV | 50 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
MatarbariTConnection_132kVtoCox'sBazar_132kV_Line2 | MatarbariTConnection_132kV | Cox'sBazar_132kV | 37 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Feni_132kVtoDaganbhuiyan_132kV_Line1 | Feni_132kV | Daganbhuiyan_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Feni_132kVtoDaganbhuiyan_132kV_Line2 | Feni_132kV | Daganbhuiyan_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Daganbhuiyan_132kVtoChowmuhani_132kV_Line1 | Daganbhuiyan_132kV | Chowmuhani_132kV | 16 | Grosbeak
Daganbhuiyan_132kVtoChowmuhani_132kV_Line2 | Daganbhuiyan_132kV | Chowmuhani_132kV | 16 | Grosbeak
Baroaulia_132kVtoKSRM_132kV_Line1 | Baroaulia_132kV | KSRM_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mymensingh_132kVtoNetrokona_132kV_Line1 | Mymensingh_132kV | Netrokona_132kV | 34 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mymensingh_132kVtoNetrokona_132kV_Line2 | Mymensingh_132kV | Netrokona_132kV | 34 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
KhulnaCentral_132kVtoNoapara_132kV_Line1 | KhulnaCentral_132kV | Noapara_132kV | 23 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
KhulnaCentral_132kVtoNoapara_132kV_Line2 | KhulnaCentral_132kV | Noapara_132kV | 23 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Noapara_132kVtoJashore_132kV_Line1 | Noapara_132kV | Jashore_132kV | 28 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Noapara_132kVtoJashore_132kV_Line2 | Noapara_132kV | Jashore_132kV | 28 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Jashore_132kVtoKaliganj_132kV_Line1 | Jashore_132kV | Kaliganj_132kV | 32 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Jashore_132kVtoKaliganj_132kV_Line2 | Jashore_132kV | Kaliganj_132kV | 32 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Kaliganj_132kVtoJhenaidahSouth_132kV_Line1 | Kaliganj_132kV | JhenaidahSouth_132kV | 15.5 | AAAC 804 sq mm
Kaliganj_132kVtoJhenaidahSouth_132kV_Line2 | Kaliganj_132kV | JhenaidahSouth_132kV | 15.5 | AAAC 804 sq mm
Jhenaidah_132kVtoKushtia_132kV_Line1 | Jhenaidah_132kV | Kushtia_132kV | 43 | AAAC 804 sq mm | 0.082575 | 0.2559 | 6.57e-06 | 132
Jhenaidah_132kVtoKushtia_132kV_Line2 | Jhenaidah_132kV | Kushtia_132kV | 43 | AAAC 804 sq mm | 0.082575 | 0.2559 | 6.57e-06 | 132
Kushtia_132kVtoBheramara_132kV_Line1 | Kushtia_132kV | Bheramara_132kV | 23 | AAAC 804 sq mm | 0.08808 | 0.2559 | 6.57e-06 | 132
Kushtia_132kVtoBheramara_132kV_Line2 | Kushtia_132kV | Bheramara_132kV | 23 | AAAC 804 sq mm | 0.08808 | 0.2559 | 6.57e-06 | 132
Bheramara_132kVtoIshwardi_132kV_Line1 | Bheramara_132kV | Ishwardi_132kV | 10 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Bheramara_132kVtoIshwardi_132kV_Line2 | Bheramara_132kV | Ishwardi_132kV | 10 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Ishwardi_132kVtoNatore_132kV_Line1 | Ishwardi_132kV | Natore_132kV | 42 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Ishwardi_132kVtoNatore_132kV_Line2 | Ishwardi_132kV | Natore_132kV | 42 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Natore_132kVtoBogura_132kV_Line1 | Natore_132kV | Bogura_132kV | 61 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Natore_132kVtoBogura_132kV_Line2 | Natore_132kV | Bogura_132kV | 61 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Bogura_132kVtoMahasthangarh_132kV_Line1 | Bogura_132kV | Mahasthangarh_132kV | 10 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Bogura_132kVtoMahasthangarh_132kV_Line2 | Bogura_132kV | Mahasthangarh_132kV | 10 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Mahasthangarh_132kVtoPalashbari_132kV_Line1 | Mahasthangarh_132kV | Palashbari_132kV | 40 | AAAC 804 sq mm | 0.1101 | 0.2559 | 6.57e-06 | 132
Mahasthangarh_132kVtoPalashbari_132kV_Line2 | Mahasthangarh_132kV | Palashbari_132kV | 40 | AAAC 804 sq mm | 0.1101 | 0.2559 | 6.57e-06 | 132
Palashbari_132kVtoMithapukur_132kV_Line1 | Palashbari_132kV | Mithapukur_132kV | 30 | AAAC 804 sq mm
Palashbari_132kVtoMithapukur_132kV_Line2 | Palashbari_132kV | Mithapukur_132kV | 30 | AAAC 804 sq mm
Mithapukur_132kVtoConfidencePP_132kV_Line1 | Mithapukur_132kV | ConfidencePP_132kV | 15 | AAAC 804 sq mm
Mithapukur_132kVtoConfidencePP_132kV_Line2 | Mithapukur_132kV | ConfidencePP_132kV | 15 | AAAC 804 sq mm
ConfidencePP_132kVtoRangpur_132kV_Line1 | ConfidencePP_132kV | Rangpur_132kV | 9 | AAAC 804 sq mm
ConfidencePP_132kVtoRangpur_132kV_Line2 | ConfidencePP_132kV | Rangpur_132kV | 9 | AAAC 804 sq mm
Rangpur_132kVtoTaraganj_132kV_Line1 | Rangpur_132kV | Taraganj_132kV | 19 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Rangpur_132kVtoTaraganj_132kV_Line2 | Rangpur_132kV | Taraganj_132kV | 19 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Taraganj_132kVtoSaidpur_132kV_Line1 | Taraganj_132kV | Saidpur_132kV | 21.5 | AAAC 804 sq mm
Taraganj_132kVtoSaidpur_132kV_Line2 | Taraganj_132kV | Saidpur_132kV | 21.5 | AAAC 804 sq mm
Saidpur_132kVtoPurbasadipur_132kV_Line1 | Saidpur_132kV | Purbasadipur_132kV | 24.5 | AAAC 804 sq mm | 0.08808 | 0.2559 | 6.57e-06 | 132
Saidpur_132kVtoPurbasadipur_132kV_Line2 | Saidpur_132kV | Purbasadipur_132kV | 24.5 | AAAC 804 sq mm | 0.08808 | 0.2559 | 6.57e-06 | 132
Purbasadipur_132kVtoThakurgaon_132kV_Line1 | Purbasadipur_132kV | Thakurgaon_132kV | 45 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Purbasadipur_132kVtoThakurgaon_132kV_Line2 | Purbasadipur_132kV | Thakurgaon_132kV | 45 | AAAC 804 sq mm | 0.09909 | 0.2559 | 6.57e-06 | 132
Rangpur_132kVtoTeestaSolar_132kV_Line1 | Rangpur_132kV | TeestaSolar_132kV | 35.7 | Grosbeak
Rangpur_132kVtoTeestaSolar_132kV_Line2 | Rangpur_132kV | TeestaSolar_132kV | 35.7 | Grosbeak
Barishal_132kVtoBhandaria_132kV_Line1 | Barishal_132kV | Bhandaria_132kV | 49 | Hawk | 0.1466 | 0.2671 | 6.29e-06 | 132
Bhandaria_132kVtoBagerhat_132kV_Line1 | Bhandaria_132kV | Bagerhat_132kV | 40 | Hawk | 0.1466 | 0.2671 | 6.29e-06 | 132
Barishal_132kVtoBakerganj_132kV_Line1 | Barishal_132kV | Bakerganj_132kV | 18 | Hawk | 0.1466 | 0.2671 | 6.29e-06 | 132
Bakerganj_132kVtoPatuakhali_132kV_Line1 | Bakerganj_132kV | Patuakhali_132kV | 20 | Hawk
Bheramara_132kVtoFaridpur_132kV_Line1 | Bheramara_132kV | Faridpur_132kV | 105 | Hawk | 0.11728 | 0.2671 | 6.29e-06 | 132
Bheramara_132kVtoFaridpur_132kV_Line2 | Bheramara_132kV | Faridpur_132kV | 105 | Hawk | 0.11728 | 0.2671 | 6.29e-06 | 132
Faridpur_132kVtoMadaripur_132kV_Line1 | Faridpur_132kV | Madaripur_132kV | 65.5 | Hawk | 0.1466 | 0.2671 | 6.29e-06 | 132
Faridpur_132kVtoMadaripur_132kV_Line2 | Faridpur_132kV | Madaripur_132kV | 65.5 | Hawk | 0.1466 | 0.2671 | 6.29e-06 | 132
Madaripur_132kVtoBarishalNorth_132kV_Line1 | Madaripur_132kV | BarishalNorth_132kV | 48.5 | Hawk | 0.1466 | 0.2671 | 6.29e-06 | 132
Madaripur_132kVtoBarishalNorth_132kV_Line2 | Madaripur_132kV | BarishalNorth_132kV | 48.5 | Hawk | 0.1466 | 0.2671 | 6.29e-06 | 132
BarishalNorth_132kVtoBarishal_132kV_Line1 | BarishalNorth_132kV | Barishal_132kV | 10 | Hawk | 0.11728 | 0.2671 | 6.29e-06 | 132
BarishalNorth_132kVtoBarishal_132kV_Line2 | BarishalNorth_132kV | Barishal_132kV | 10 | Hawk | 0.11728 | 0.2671 | 6.29e-06 | 132
Ishwardi_132kVtoBaghabari_132kV_Line1 | Ishwardi_132kV | Baghabari_132kV | 63 | Hawk | 0.1466 | 0.2671 | 6.29e-06 | 132
Baghabari_132kVtoUllapara_132kV_Line1 | Baghabari_132kV | Ullapara_132kV | 17 | Grosbeak | 0.1466 | 0.2671 | 6.29e-06 | 132
Shahjadpur_132kVtoUllapara_132kV_Line1 | Shahjadpur_132kV | Ullapara_132kV | 13 | Grosbeak
Ishwardi_132kVtoPabna_132kV_Line1 | Ishwardi_132kV | Pabna_132kV | 18 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Pabna_132kVtoShahjadpur_132kV_Line1 | Pabna_132kV | Shahjadpur_132kV | 41 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Bogura_132kVtoSirajganj_132kV_Line1 | Bogura_132kV | Sirajganj_132kV | 66 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Bogura_132kVtoSirajganj_132kV_Line2 | Bogura_132kV | Sirajganj_132kV | 66 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sirajganj_132kVtoShahjadpur_132kV_Line1 | Sirajganj_132kV | Shahjadpur_132kV | 34 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sirajganj_132kVtoBaghabari_132kV_Line1 | Sirajganj_132kV | Baghabari_132kV | 40 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rajshahi_132kVtoRajshahiNorth_132kV_Line1 | Rajshahi_132kV | RajshahiNorth_132kV | 48 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rajshahi_132kVtoRajshahiNorth_132kV_Line2 | Rajshahi_132kV | RajshahiNorth_132kV | 48 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rangpur_132kVtoLalmonirhat_132kV_Line1 | Rangpur_132kV | Lalmonirhat_132kV | 38 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Bogura_132kVtoNaogaon_132kV_Line1 | Bogura_132kV | Naogaon_132kV | 44 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Bogura_132kVtoNaogaon_132kV_Line2 | Bogura_132kV | Naogaon_132kV | 44 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Kabirpur_132kVtoTangail_132kV_Line1 | Kabirpur_132kV | Tangail_132kV | 51 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kabirpur_132kVtoTangail_132kV_Line2 | Kabirpur_132kV | Tangail_132kV | 51 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Tongi_132kVtoMirpur_132kV_Line1 | Tongi_132kV | Mirpur_132kV | 17 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Tongi_132kVtoUttara_132kV_Line1 | Tongi_132kV | Uttara_132kV | 15 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Uttara_132kVtoMirpur_132kV_Line1 | Uttara_132kV | Mirpur_132kV | 9 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Mirpur_132kVtoAminbazar_132kV_Line1 | Mirpur_132kV | Aminbazar_132kV | 7 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Mirpur_132kVtoAminbazar_132kV_Line2 | Mirpur_132kV | Aminbazar_132kV | 7 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Aminbazar_132kVtoKallayanpur_132kV_Line1 | Aminbazar_132kV | Kallayanpur_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Aminbazar_132kVtoKallayanpur_132kV_Line2 | Aminbazar_132kV | Kallayanpur_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kallayanpur_132kVtoLalbagh_132kV_Line1 | Kallayanpur_132kV | Lalbagh_132kV | 8 | Grosbeak
Kallayanpur_132kVtoLalbagh_132kV_Line2 | Kallayanpur_132kV | Lalbagh_132kV | 8 | Grosbeak
Lalbagh_132kVtoKeraniganj_132kV_Line1 | Lalbagh_132kV | Keraniganj_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Keraniganj_132kVtoKamrangirchar_132kV_Line1 | Keraniganj_132kVt | Kamrangirchar_132kV | 3 | Grosbeak
Kamrangirchar_132kVtoLalbagh_132kV_Line1 | Kamrangirchar_132kV | Lalbagh_132kV | 3 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Hasnabad_132kVtoKeraniganj_132kV_Line1 | Hasnabad_132kV | Keraniganj_132kV | 14 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Hasnabad_132kVtoKeraniganj_132kV_Line2 | Hasnabad_132kV | Keraniganj_132kV | 14 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Tongi_132kVtoNewTongi_132kV_Line1 | Tongi_132kV | NewTongi_132kV | 0.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Tongi_132kVtoNewTongi_132kV_Line2 | Tongi_132kV | NewTongi_132kV | 0.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Hasnabad_132kVtoSitalakhya_132kV_Line1 | Hasnabad_132kV | Sitalakhya_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madanganj_132kVtoSitalakhya_132kV_Line1 | Madanganj_132kV | Sitalakhya_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Hasnabad_132kVtoFatullah_132kV_Line1 | Hasnabad_132kV | Fatullah_132kV | 21 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Fatullah_132kVtoHaripur_132kV_Line1 | Fatullah_132kV | Haripur_132kV | 5 | Grosbeak
Madanganj_132kVtoHaripur_132kV_Line1 | Madanganj_132kV | Haripur_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Siddhirganj_132kVtoUllon_132kV_Line1 | Siddhirganj_132kV | Ullon_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Siddhirganj_132kVtoUllon_132kV_Line2 | Siddhirganj_132kV | Ullon_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Siddhirganj_132kVoMatuail_132kV_Line1 | Siddhirganj_132kV | Matuail_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Maniknagar_132kVtoMatuail_132kV_Line1 | Maniknagar_132kV | Matuail_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Siddhirganj_132kVtoManiknagar_132kV_Line1 | Siddhirganj_132kV | Maniknagar_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Maniknagar_132kVtoNarinda_132kV_Line1 | Maniknagar_132kV | Narinda_132kV | 5 | Cu 240 sq mm | 0.075 | 0.13 | 2e-05 | 132
Maniknagar_132kVtoNarinda_132kV_Line2 | Maniknagar_132kV | Narinda_132kV | 5 | Cu 240 sq mm | 0.075 | 0.13 | 2e-05 | 132
Ullon_132kVtoDhanmondi_132kV_Line1 | Ullon_132kV | Dhanmondi_132kV | 5.5 | Cu 240 sq mm | 0.075 | 0.13 | 2e-05 | 132
Ullon_132kVtoDhanmondi_132kV_Line2 | Ullon_132kV | Dhanmondi_132kV | 5.5 | Cu 240 sq mm | 0.075 | 0.13 | 2e-05 | 132
Ullon_132kVtoDhanmondi_132kV_Line3 | Ullon_132kV | Dhanmondi_132kV | 5.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Ullon_132kVtoDhanmondi_132kV_Line4 | Ullon_132kV | Dhanmondi_132kV | 5.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Tongi_132kVtoKabirpur_132kV_Line1 | Tongi_132kV | Kabirpur_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Tongi_132kVtoKabirpur_132kV_Line2 | Tongi_132kV | Kabirpur_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kabirpur_132kVtoManikganj_132kV_Line1 | Kabirpur_132kV | Manikganj_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kabirpur_132kVtoManikganj_132kV_Line2 | Kabirpur_132kV | Manikganj_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ullon_132kVtoRampura_132kV_Line1 | Ullon_132kV | Rampura_132kV | 4 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Ullon_132kVtoRampura_132kV_Line2 | Ullon_132kV | Rampura_132kV | 4 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoBashundhara_132kV_Line1 | Rampura_132kV | Bashundhara_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rampura_132kVtoBashundhara_132kV_Line2 | Rampura_132kV | Bashundhara_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Bashundhara_132kVtoTongi_132kV_Line1 | Bashundhara_132kV | Tongi_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Bashundhara_132kVtoTongi_132kV_Line2 | Bashundhara_132kV | Tongi_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rampura_132kVtoMoghbazar_132kV_Line1 | Rampura_132kV | Moghbazar_132kV | 4.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rampura_132kVtoMoghbazar_132kV_Line2 | Rampura_132kV | Moghbazar_132kV | 4.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ghorashal_132kVtoPubail_132kV_Line1 | Ghorashal_132kV | Pubail_132kV | 17.1 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ghorashal_132kVtoPubail_132kV_Line2 | Ghorashal_132kV | Pubail_132kV | 17.1 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Pubail_132kVtoJoydebpur_132kV_Line1 | Pubail_132kV | Joydebpur_132kV | 17.1 | Grosbeak
Pubail_132kVtoJoydebpur_132kV_Line2 | Pubail_132kV | Joydebpur_132kV | 17.1 | Grosbeak
Baghabari_132kVtoShahjadpur_132kV_Line1 | Baghabari_132kV | Shahjadpur_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Baghabari_132kVtoShahjadpur_132kV_Line2 | Baghabari_132kV | Shahjadpur_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chandpur_132kVtoDeshPP_132kV_Line1 | Chandpur_132kV | DeshPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chandpur_132kVtoDeshPP_132kV_Line2 | Chandpur_132kV | DeshPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
DeshPP_132kVtoRamganj_132kV_Line1 | DeshPP_132kV | Ramganj_132kV | 28 | Grosbeak
DeshPP_132kVtoRamganj_132kV_Line2 | DeshPP_132kV | Ramganj_132kV | 28 | Grosbeak
Ramganj_132kVtoChowmuhani_132kV_Line1 | Ramganj_132kV | Chowmuhani_132kV | 39 | Grosbeak
Ramganj_132kVtoChowmuhani_132kV_Line2 | Ramganj_132kV | Chowmuhani_132kV | 39 | Grosbeak
Barapukuria_132kVtoRangpur_132kV_Line1 | Barapukuria_132kV | Rangpur_132kV | 42 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Barapukuria_132kVtoRangpur_132kV_Line2 | Barapukuria_132kV | Rangpur_132kV | 42 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Barapukuria_132kVtoSaidpur_132kV_Line1 | Barapukuria_132kV | Saidpur_132kV | 36 | Grosbeak | 0.082575 | 0.2559 | 6.57e-06 | 132
Barapukuria_132kVtoSaidpur_132kV_Line2 | Barapukuria_132kV | Saidpur_132kV | 36 | Grosbeak | 0.082575 | 0.2559 | 6.57e-06 | 132
Madaripur_132kVtoGopalganjNorth_132kV_Line1 | Madaripur_132kV | GopalganjNorth_132kV | 23 | Grosbeak | 0.09909 | 0.2559 | 6.57e-06 | 132
Madaripur_132kVtoGopalganjNorth_132kV_Line2 | Madaripur_132kV | GopalganjNorth_132kV | 23 | Grosbeak
Madaripur_132kVtoGopalganjNorth_132kV_Line3 | Madaripur_132kV | GopalganjNorth_132kV | 23 | Grosbeak
Madaripur_132kVtoGopalganjNorth_132kV_Line4 | Madaripur_132kV | GopalganjNorth_132kV | 23 | Grosbeak
GopalganjNorth_132kVtoGopalganj_132kV_Line1 | GopalganjNorth_132kV | Gopalganj_132kV | 35 | Grosbeak
GopalganjNorth_132kVtoGopalganj_132kV_Line2 | GopalganjNorth_132kV | Gopalganj_132kV | 35 | Grosbeak
GopalganjNorth_132kVtoFaridpur_132kV_Line1 | GopalganjNorth_132kV | Faridpur_132kV | 20 | Grosbeak
GopalganjNorth_132kVtoFaridpur_132kV_Line2 | GopalganjNorth_132kV | Faridpur_132kV | 20 | Grosbeak
Faridpur_132kVtoRajbari_132kV_Line1 | Faridpur_132kV | Rajbari_132kV | 55 | Grosbeak
Faridpur_132kVtoRajbari_132kV_Line2 | Faridpur_132kV | Rajbari_132kV | 55 | Grosbeak
Rajbari_132kVtoBheramara_132kV_Line1 | Rajbari_132kV | Bheramara_132kV | 98 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rajbari_132kVtoBheramara_132kV_Line2 | Rajbari_132kV | Bheramara_132kV | 98 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
KhulnaCentral_132kVtoKhulnaSouth_132kV_Line1 | KhulnaCentral_132kV | KhulnaSouth_132kV | 9 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 132
KhulnaCentral_132kVtoKhulnaSouth_132kV_Line2 | KhulnaCentral_132kV | KhulnaSouth_132kV | 9 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 132
KhulnaSouth_132kVtoSatkhira_132kV_Line1 | KhulnaSouth_132kV | Satkhira_132kV | 47 | Grosbeak | 0.09909 | 0.2559 | 6.57e-06 | 132
KhulnaSouth_132kVtoSatkhira_132kV_Line2 | KhulnaSouth_132kV | Satkhira_132kV | 47 | Grosbeak | 0.09909 | 0.2559 | 6.57e-06 | 132
Rajshahi_132kVtoNatore_132kV_Line1 | Rajshahi_132kV | Natore_132kV | 37 | Hawk | 0.1101 | 0.2559 | 6.57e-06 | 132
Rajshahi_132kVtoNatore_132kV_Line2 | Rajshahi_132kV | Natore_132kV | 40 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rampura_132kVtoGulshan_132kV_Line1 | Rampura_132kV | Gulshan_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoGulshan_132kV_Line2 | Rampura_132kV | Gulshan_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Sikalbaha_132kVtoBakulia_132kV_Line1 | Sikalbaha_132kV | Bakulia_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sikalbaha_132kVtoBakulia_132kV_Line2 | Sikalbaha_132kV | Bakulia_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Juldah_132kVtoShahmirpur_132kV_Line1 | Juldah_132kV | Shahmirpur_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Juldah_132kVtoShahmirpur_132kV_Line2 | Juldah_132kV | Shahmirpur_132kV | 6 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Khulshi_132kVtoBakulia_132kV_Line1 | Khulshi_132kV | Bakulia_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Khulshi_132kVtoMSML_132kV_Line1 | Khulshi_132kV | MSML_132kV | 7.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
MSML_132kVtoBakulia_132kV_Line1 | MSML_132kV | Bakulia_132kV | 7.5 | Grosbeak
Haripur_132kVtoManiknagar_132kV_Line1 | Haripur_132kV | Maniknagar_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Joydebpur_132kVtoKodda_132kV_Line1 | Joydebpur_132kV | Kodda_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Joydebpur_132kVtoKodda_132kV_Line2 | Joydebpur_132kV | Kodda_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kodda_132kVtoKabirpur_132kV_Line1 | Kodda_132kV | Kabirpur_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kodda_132kVtoKabirpur_132kV_Line2 | Kodda_132kV | Kabirpur_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sikalbaha_132kVtoShahmirpur_132kV_Line1 | Sikalbaha_132kV | Shahmirpur_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sikalbaha_132kVtoShahmirpur_132kV_Line2 | Sikalbaha_132kV | Shahmirpur_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Khulshi_132kVtoHalishahar_132kV_Line1 | Khulshi_132kV | Halishahar_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Khulshi_132kVtoHalishahar_132kV_Line2 | Khulshi_132kV | Halishahar_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Khulshi_132kVtoRampur_132kV_Line1 | Khulshi_132kV | Rampur_132kV | 5 | Grosbeak
Khulshi_132kVtoRampur_132kV_Line2 | Khulshi_132kV | Rampur_132kV | 5 | Grosbeak
Rampur_132kVtoHalishahar_132kV_Line1 | Rampur_132kV | Halishahar_132kV | 9 | Grosbeak
Rampur_132kVtoHalishahar_132kV_Line2 | Rampur_132kV | Halishahar_132kV | 9 | Grosbeak
BoguraSouth_132kVtoBogura_132kV_Line1 | BoguraSouth_132kV | Bogura_132kV | 1.5 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 132
BoguraSouth_132kVtoBogura_132kV_Line2 | BoguraSouth_132kV | Bogura_132kV | 1.5 | Twin AAAC | 0.049545 | 0.14064 | 1.31e-05 | 132
Ashuganj_132kVtoShahjibazar_132kV_Line1 | Ashuganj_132kV | Shahjibazar_132kV | 53 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
KhulnaSouth_132kVtoGallamari_132kV_Line1 | KhulnaSouth_132kV | Gallamari_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
KhulnaSouth_132kVtoGallamari_132kV_Line2 | KhulnaSouth_132kV | Gallamari_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Naogaon_132kVtoNiamatpur_132kV_Line1 | Naogaon_132kV | Niamatpur_132kV | 46 | Grosbeak | 0.09909 | 0.2559 | 6.57e-06 | 132
Aminbazar_132kVtoSavar_132kV_Line1 | Aminbazar_132kV | Savar_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Aminbazar_132kVtoSavar_132kV_Line2 | Aminbazar_132kV | Savar_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Jhenaidah_132kVtoMagura_132kV_Line1 | Jhenaidah_132kV | Magura_132kV | 26.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Jhenaidah_132kVtoMagura_132kV_Line2 | Jhenaidah_132kV | Magura_132kV | 26.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Jhenaidah_132kVtoJhenaidahSouth_132kV_Line1 | Jhenaidah_132kV | JhenaidahSouth_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
JhenaidahSouth_132kVtoChuadanga_132kV_Line1 | JhenaidahSouth_132kV | Chuadanga_132kV | 39 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Thakurgaon_132kVtoPanchagarh_132kV_Line1 | Thakurgaon_132kV | Panchagarh_132kV | 45 | Grosbeak | 0.09909 | 0.2559 | 6.57e-06 | 132
Thakurgaon_132kVtoPanchagarh_132kV_Line2 | Thakurgaon_132kV | Panchagarh_132kV | 45 | Grosbeak | 0.09909 | 0.2559 | 6.57e-06 | 132
Sonargaon_132kVtoMeghnaghatRentalPP_132kV_Line1 | Sonargaon_132kV | MeghnaghatRentalPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sonargaon_132kVtoMeghnaghatRentalPP_132kV_Line2 | Sonargaon_132kV | MeghnaghatRentalPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Siddhirganj_132kVtoSiddhirganjDutchBanglaPP_132kV_Line1 | Siddhirganj_132kV | SiddhirganjDutchBanglaPP_132kV | 2 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Goalpara_132kVtoKhulnaCentral_132kV_Line1 | Goalpara_132kV | KhulnaCentral_132kV | 2 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
Goalpara_132kVtoKhulnaCentral_132kV_Line2 | Goalpara_132kV | KhulnaCentral_132kV | 2 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
Noapara_132kVtoNoaparaPP_132kV_Line1 | Noapara_132kV | NoaparaPP_132kV | 2 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Daudkandi_132kVtoDaudkandiPP_132kV_Line1 | Daudkandi_132kV | DaudkandiPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Gopalganj_132kVtoGopalganjPP_132kV_Line1 | Gopalganj_132kV | GopalganjPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Siddhirganj_132kVtoSiddhirganjDeshEnergyPP_132kV_Line1 | Siddhirganj_132kV | SiddhirganjDeshEnergyPP_132kV | 3 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Faridpur_132kVtoFaridpurPP_132kV_Line1 | Faridpur_132kV | FaridpurPP_132kV | 1 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Baghabari_132kVtoSathia_132kV_Line1 | Baghabari_132kV | Sathia_132kV | 11 | Grosbeak
Sathia_132kVtoBeraPP_132kV_Line1 | Sathia_132kV | BeraPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
BeraPP_132kVtoIshwardi_132kV_Line1 | BeraPP_132kV | Ishwardi_132kV | 67 | Grosbeak
RajshahiNorth_132kVtoChapaiNawabganj_132kV_Line1 | RajshahiNorth_132kV | ChapaiNawabganj_132kV | 45 | Grosbeak
RajshahiNorth_132kVtoAmnura_132kV_Line1 | RajshahiNorth_132kV | Amnura_132kV | 30 | Grosbeak
Amnura_132kVtoChapaiNawabganj_132kV_Line1 | Amnura_132kV | ChapaiNawabganj_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madanganj_132kVtoMunshiganj_132kV_Line1 | Madanganj_132kV | Munshiganj_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madanganj_132kVtoMunshiganj_132kV_Line2 | Madanganj_132kV | Munshiganj_132kV | 4 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Agargaon_132kVtoCantonment_132kV_Line1 | Agargaon_132kV | Cantonment_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Agargaon_132kVtoCantonment_132kV_Line2 | Agargaon_132kV | Cantonment_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Fenchuganj_132kVtoKulaura_132kV_Line1 | Fenchuganj_132kV | Kulaura_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Fenchuganj_132kVtoKulaura_132kV_Line2 | Fenchuganj_132kV | Kulaura_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Jamalpur_132kVtoUnitedPP_132kV_Line1 | Jamalpur_132kV | UnitedPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Jamalpur_132kVtoUnitedPP_132kV_Line2 | Jamalpur_132kV | UnitedPP_132kV | 5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
UnitedPP_132kVtoSherpur_132kV_Line1 | UnitedPP_132kV | Sherpur_132kV | 15 | Grosbeak
UnitedPP_132kVtoSherpur_132kV_Line2 | UnitedPP_132kV | Sherpur_132kV | 15 | Grosbeak
Agargaon_132kVtoSatmasjid_132kV_Line1 | Agargaon_132kV | Satmasjid_132kV | 8.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Agargaon_132kVtoSatmasjid_132kV_Line2 | Agargaon_132kV | Satmasjid_132kV | 8.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoMadartek_132kV_Line1 | Rampura_132kV | Madartek_132kV | 4.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoMadartek_132kV_Line2 | Rampura_132kV | Madartek_132kV | 4.5 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
CumillaNorth_132kVtoCumillaSouth_132kV_Line1 | CumillaNorth_132kV | CumillaSouth_132kV | 19 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaNorth_132kVtoCumillaSouth_132kV_Line2 | CumillaNorth_132kV | CumillaSouth_132kV | 19 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaNorth_132kVtoCumillaSouth_132kV_Line3 | CumillaNorth_132kV | CumillaSouth_132kV | 19 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Goalpara_132kVtoBagerhat_132kV_Line1 | Goalpara_132kV | Bagerhat_132kV | 45 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Goalpara_132kVtoLabancharaPP_132kV_Line1 | Goalpara_132kV | LabancharaPP_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
LabancharaPP_132kVtoBagerhat_132kV_Line1 | LabancharaPP_132kV | Bagerhat_132kV | 22.5 | Grosbeak
Kabirpur_132kVtoKaliakoir_132kV_Line1 | Kabirpur_132kV | Kaliakoir_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kabirpur_132kVtoKaliakoir_132kV_Line2 | Kabirpur_132kV | Kaliakoir_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kaliakoir_132kVtoMirzapur_132kV_Line1 | Kaliakoir_132kV | Mirzapur_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kaliakoir_132kVtoMirzapur_132kV_Line2 | Kaliakoir_132kV | Mirzapur_132kV | 13 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mirzapur_132kVtoTangail_132kV_Line1 | Mirzapur_132kV | Tangail_132kV | 93.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mirzapur_132kVtoTangail_132kV_Line2 | Mirzapur_132kV | Tangail_132kV | 93.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Tangail_132kVtoGhatail_132kV_Line1 | Tangail_132kV | Ghatail_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Tangail_132kVtoGhatail_132kV_Line2 | Tangail_132kV | Ghatail_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ghatail_132kVtoMukhtagacha_132kV_Line1 | Ghatail_132kV | Mukhtagacha_132kV | 42 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ghatail_132kVtoMukhtagacha_132kV_Line2 | Ghatail_132kV | Mukhtagacha_132kV | 42 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mukhtagacha_132kVtoRPCLPP_132kV_Line1 | Mukhtagacha_132kV | RPCLPP_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mukhtagacha_132kVtoRPCLPP_132kV_Line2 | Mukhtagacha_132kV | RPCLPP_132kV | 12 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
RPCLPP_132kVtoMymensingh_132kV_Line1 | RPCLPP_132kV | Mymensingh_132kV | 4 | Grosbeak
RPCLPP_132kVtoMymensingh_132kV_Line2 | RPCLPP_132kV | Mymensingh_132kV | 4 | Grosbeak
Kaliakoir_132kVtoDhamrai_132kV_Line1 | Kaliakoir_132kV | Dhamrai_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kaliakoir_132kVoDhamrai_132kV_Line2 | Kaliakoir_132kV | Dhamrai_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rangamati_132kVtoKhagrachari_132kV_Line1 | Rangamati_132kV | Khagrachari_132kV | 52.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rangamati_132kVtoKhagrachari_132kV_Line2 | Rangamati_132kV | Khagrachari_132kV | 52.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chandraghona_132kVtoRangamati_132kV_Line1 | Chandraghona_132kV | Rangamati_132kV | 27.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chandraghona_132kVtoRangamati_132kV_Line2 | Chandraghona_132kV | Rangamati_132kV | 27.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chhatak_132kVtoSunamganj_132kV_Line1 | Chhatak_132kV | Sunamganj_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chhatak_132kVtoSunamganj_132kV_Line2 | Chhatak_132kV | Sunamganj_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Beanibazar_132kVtoSylhetSouth_132kV_Line1 | Beanibazar_132kV | SylhetSouth_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Beanibazar_132kVtoSylhetSouth_132kV_Line2 | Beanibazar_132kV | SylhetSouth_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mirpur_132kVtoUttara3P_132kV_Line1 | Mirpur_132kV | Uttara3P_132kV | 5 | Grosbeak
Uttara 3P_132kVtoTongi_132kV_Line1 | Uttara 3P_132kV | Tongi_132kV | 2 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
MatarbariTConnection_132kVtoMatarbari_132kV_Line1 | MatarbariTConnection_132kV | Matarbari_132kV | 18 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Feni_132kVtoBaroirhat_132kV_Line1 | Feni_132kV | Baroirhat_132kV | 28.5 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Feni_132kVtoPHP_132kV_Line1 | Feni_132kV | PHP_132kV | 17 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
PHP_132kVtoBaroirhat_132kV_Line1 | PHP_132kV | Baroirhat_132kV | 11.5 | Grosbeak
Brahmanbaria_132kVtoNarsingdi_132kV_Line1 | Brahmanbaria_132kV | Narsingdi_132kV | 55 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Brahmanbaria_132kVtoNarsingdi_132kV_Line2 | Brahmanbaria_132kV | Narsingdi_132kV | 55 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Saidpur_132kVtoJaldhaka_132kV_Line1 | Saidpur_132kV | Jaldhaka_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Saidpur_132kVtoJaldhaka_132kV_Line2 | Saidpur_132kV | Jaldhaka_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rooppur_132kVtoIshwardi_132kV_Line1 | Rooppur_132kV | Ishwardi_132kV | 7 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rooppur_132kVtoIshwardi_132kV_Line2 | Rooppur_132kV | Ishwardi_132kV | 7 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mymensingh_132kVtoBhaluka_132kV_Line1 | Mymensingh_132kV | Bhaluka_132kV | 43 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Mymensingh_132kVtoBhaluka_132kV_Line2 | Mymensingh_132kV | Bhaluka_132kV | 43 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
MadhumatiPP_132kVtoGopalganj_132kV_Line1 | MadhumatiPP_132kV | Gopalganj_132kV | 15 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Jashore_132kVtoBenapole_132kV_Line1 | Jashore_132kV | Benapole_132kV | 30.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Jashore_132kVtoBenapole_132kV_Line2 | Jashore_132kV | Benapole_132kV | 30.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madaripur_132kVtoShariatpur_132kV_Line1 | Madaripur_132kV | Shariatpur_132kV | 22 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Madaripur_132kVtoShariatpur_132kV_Line2 | Madaripur_132kV | Shariatpur_132kV | 22 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rangpur_132kVtoKurigram_132kV_Line1 | Rangpur_132kV | Kurigram_132kV | 41 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Magura_132kVtoNarail_132kV_Line1 | Magura_132kV | Narail_132kV | 39.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Magura_132kVtoNarail_132kV_Line2 | Magura_132kV | Narail_132kV | 39.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
BoguraSouth_132kVtoSherpur(B)_132kV_Line1 | BoguraSouth_132kV | Sherpur(B)_132kV | 24 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
BoguraSouth_132kVtoSherpur(B)_132kV_Line2 | BoguraSouth_132kV | Sherpur(B)_132kV | 24 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sherpur(B)_132kVtoSirajganj_132kV_Line1 | Sherpur(B)_132kV | Sirajganj_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sherpur(B)_132kVtoSirajganj_132kV_Line2 | Sherpur(B)_132kV | Sirajganj_132kV | 33 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rampura_132kVtoAftabnagar_132kV_Line1 | Rampura_132kV | Aftabnagar_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoAftabnagar_132kV_Line2 | Rampura_132kV | Aftabnagar_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoHatirjheel_132kV_Line1 | Rampura_132kV | Hatirjheel_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoHatirjheel_132kV_Line2 | Rampura_132kV | Hatirjheel_132kV | 3.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
CumillaSouth_132kVtoChauddagram_132kV_Line1 | CumillaSouth_132kV | Chauddagram_132kV | 29 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaSouth_132kVtoChauddagram_132kV_Line2 | CumillaSouth_132kV | Chauddagram_132kV | 29 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chauddagram_132kVtoFeniNorth_132kV_Line1 | Chauddagram_132kV | FeniNorth_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chauddagram_132kVtoFeniNorth_132kV_Line2 | Chauddagram_132kV | FeniNorth_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
FeniNorth_132kVtoFeni_132kV_Line1 | FeniNorth_132kV | Feni_132kV | 4 | Grosbeak
FeniNorth_132kVtoFeni_132kV_Line2 | FeniNorth_132kV | Feni_132kV | 4 | Grosbeak
Kodda_132kVtoRajendrapur_132kV_Line1 | Kodda_132kV | Rajendrapur_132kV | 24.5 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Kodda_132kVtoRajendrapur_132kV_Line2 | Kodda_132kV | Rajendrapur_132kV | 24.5 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Rampur_132kVtoAgrabad_132kV_Line1 | Rampur_132kV | Agrabad_132kV | 4.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampur_132kVtoAgrabad_132kV_Line2 | Rampur_132kV | Agrabad_132kV | 4.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Keraniganj_132kVtoSrinagar_132kV_Line1 | Keraniganj_132kV | Srinagar_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Keraniganj_132kVtoSrinagar_132kV_Line2 | Keraniganj_132kV | Srinagar_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Keraniganj_132kVtoNawabganj_132kV_Line1 | Keraniganj_132kV | Nawabganj_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Keraniganj_132kVtoNawabganj_132kV_Line2 | Keraniganj_132kV | Nawabganj_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Fatullah_132kVtoShyampur_132kV_Line1 | Fatullah_132kV | Shyampur_132kV | 4 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
Fatullah_132kVtoShyampur_132kV_Line2 | Fatullah_132kV | Shyampur_132kV | 4 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
DhakaUniversity_132kVtoDhanmondi_132kV_Line1 | DhakaUniversity_132kV | Dhanmondi_132kV | 2 | XLPE 500 sq mm | 0.015 | 0.12 | 2e-05 | 132
DhakaUniversity_132kVtoDhanmondi_132kV_Line2 | DhakaUniversity_132kV | Dhanmondi_132kV | 2 | Grosbeak | 0.015 | 0.12 | 2e-05 | 132
Bagerhat_132kVtoMongla_132kV_Line1 | Bagerhat_132kV | Mongla_132kV | 28.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Bagerhat_132kVtoMongla_132kV_Line2 | Bagerhat_132kV | Mongla_132kV | 28.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Baghabari_132kVtoBhangura_132kV_Line1 | Baghabari_132kV | Bhangura_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Baghabari_132kVtoBhangura_132kV_Line2 | Baghabari_132kV | Bhangura_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Bakerganj_132kVtoBarguna_132kV_Line1 | Bakerganj_132kV | Barguna_132kV | 50 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Gallamari_132kVtoGopalganj_132kV_Line1 | Gallamari_132kV | Gopalganj_132kV | 52 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Gallamari_132kVtoGopalganj_132kV_Line2 | Gallamari_132kV | Gopalganj_132kV | 52 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Maniknagar_132kVtoKazla_132kV_Line1 | Maniknagar_132kV | Kazla_132kV | 2.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Maniknagar_132kVtoKazla_132kV_Line2 | Maniknagar_132kV | Kazla_132kV | 2.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Purbachal_132kVtoBashundhara_132kV_Line1 | Purbachal_132kV | Bashundhara_132kV | 4.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Purbachal_132kVtoBashundhara_132kV_Line2 | Purbachal_132kV | Bashundhara_132kV | 4.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Banani_132kVtoBashundhara_132kV_Line1 | Banani_132kV | Bashundhara_132kV | 13.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Banani_132kVtoBashundhara_132kV_Line2 | Banani_132kV | Bashundhara_132kV | 13.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rajbari_132kVtoBheramara_132kV_Line3 | Rajbari_132kV | Bheramara_132kV | 1.25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rajbari_132kVtoBheramara_132kV_Line4 | Rajbari_132kV | Bheramara_132kV | 1.25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Tongi_132kVtoTongi-3(Mill Gate)_132kV_Line1 | Tongi_132kV | Tongi-3(Mill Gate)_132kV | 2.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Tongi_132kVtoTongi-3(Mill Gate)_132kV_Line2 | Tongi_132kV | Tongi-3(Mill Gate)_132kV | 2.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Jhenaidah_132kVtoJhenaidahSouth_132kV_Line2 | Jhenaidah_132kV | JhenaidahSouth_132kV | 5 | Grosbeak
Jhenaidah_132kVtoJhenaidahSouth_132kV_Line3 | Jhenaidah_132kV | JhenaidahSouth_132kV | 5 | Grosbeak
JhenaidahSouth_132kVtoJashore_132kV_Line1 | JhenaidahSouth_132kV | Jashore_132kV | 43 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
JhenaidahSouth_132kVtoJashore_132kV_Line2 | JhenaidahSouth_132kV | Jashore_132kV | 43 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Maniknagar_132kVtoMotijheel_132kV_Line1 | Maniknagar_132kV | Motijheel_132kV | 2 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Maniknagar_132kVtoMotijheel_132kV_Line2 | Maniknagar_132kV | Motijheel_132kV | 2 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Motijheel_132kVtoBangabhaban_132kV_Line1 | Motijheel_132kV | Bangabhaban_132kV | 0.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Motijheel_132kVtoBangabhaban_132kV_Line2 | Motijheel_132kV | Bangabhaban_132kV | 0.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Madanganj_132kVtoCharSaidpur_132kV_Line1 | Madanganj_132kV | CharSaidpur_132kV | 3 | XLPE 800 sq mm | 0.08831 | 0.2441 | 6.87e-06 | 132
Madanganj_132kVtoCharSaidpur_132kV_Line2 | Madanganj_132kV | CharSaidpur_132kV | 3 | XLPE 800 sq mm | 0.08831 | 0.2441 | 6.87e-06 | 132
Kamrangirchar_132kVtoZigatola_132kV_Line1 | Kamrangirchar_132kV | Zigatola_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Kamrangirchar_132kVtoZigatola_132kV_Line2 | Kamrangirchar_132kV | Zigatola_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Energon_132kVtoMongla_132kV_Line1 | Energon_132kV | Mongla_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Hasnabad_132kVtoPostagola_132kV_Line1 | Hasnabad_132kV | Postagola_132kV | 2 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Hasnabad_132kVtoPostagola_132kV_Line2 | Hasnabad_132kV | Postagola_132kV | 2 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Banani_132kVtoPurbachal_132kV_Line1 | Banani_132kV | Purbachal_132kV | 5.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Banani_132kVtoPurbachal_132kV_Line2 | Banani_132kV | Purbachal_132kV | 5.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
ChapaiNawabganj_132kVtoRahanpur_132kV_Line1 | ChapaiNawabganj_132kV | Rahanpur_132kV | 25.9 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
ChapaiNawabganj_132kVtoRahanpur_132kV_Line2 | ChapaiNawabganj_132kV | Rahanpur_132kV | 25.9 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Madunaghat_132kVtoKalurghat_132kV_Line1 | Madunaghat_132kV | Kalurghat_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Madunaghat_132kVtoKalurghat_132kV_Line2 | Madunaghat_132kV | Kalurghat_132kV | 7 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoDhakaUniversity_132kV_Line1 | Rampura_132kV | DhakaUniversity_132kV | 7.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Rampura_132kVtoDhakaUniversity_132kV_Line2 | Rampura_132kV | DhakaUniversity_132kV | 7.5 | XLPE 800 sq mm | 0.015 | 0.12 | 2e-05 | 132
Sripur_132kVtoBhaluka_132kV_Line1 | Sripur_132kV | Bhaluka_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sripur_132kVtoBhaluka_132kV_Line2 | Sripur_132kV | Bhaluka_132kV | 22.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ullapara_132kVtoSirajganj_132kV_Line1 | Ullapara_132kV | Sirajganj_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Ullapara_132kVtoSirajganj_132kV_Line2 | Ullapara_132kV | Sirajganj_132kV | 25 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Bhaluka_132kVtoBarmiPP_132kV_Line1 | Bhaluka_132kV | BarmiPP_132kV | 32.5 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Bhaluka_132kVtoBarmiPP_132kV_Line2 | Bhaluka_132kV | BarmiPP_132kV | 32.5 | Grosbeak | 0.08808 | 0.2559 | 6.57e-06 | 132
Niamatpur_132kVtoRahanpur_132kV_Line1 | Niamatpur_132kV | Rahanpur_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Niamatpur_132kVtoRahanpur_132kV_Line2 | Niamatpur_132kV | Rahanpur_132kV | 30 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Naogaon_132kVtoJoypurhat_132kV_Line1 | Naogaon_132kV | Joypurhat_132kV | 47 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Naogaon_132kVtoJoypurhat_132kV_Line2 | Naogaon_132kV | Joypurhat_132kV | 47 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Cox'sBazar_132kVtoUSDKWindFarm_132kV_Line1 | Cox'sBazar_132kV | USDKWindFarm_132kV | 11 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
BarishalNorth_132kVtoBhandaria_132kV_Line1 | BarishalNorth_132kV | Bhandaria_132kV | 46.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
BarishalNorth_132kVtoBhandaria_132kV_Line2 | BarishalNorth_132kV | Bhandaria_132kV | 46.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sirajganj68MWSolar_132kVtoSirajganj_132kV_Line1 | Sirajganj68MWSolar_132kV | Sirajganj_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sirajganj68MWSolar_132kVtoSirajganj_132kV_Line2 | Sirajganj68MWSolar_132kV | Sirajganj_132kV | 10 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rahanpur_132kVtoChowdala_132kV_Line1 | Rahanpur_132kV | Chowdala_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rahanpur_132kVtoChowdala_132kV_Line2 | Rahanpur_132kV | Chowdala_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Muradnagar_132kVtoKosba_132kV_Line1 | Muradnagar_132kV | Kosba_132kV | 24 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Muradnagar_132kVtoKosba_132kV_Line2 | Muradnagar_132kV | Kosba_132kV | 24 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Jhenaidah_132kVtoChuadanga_132kV_Line1 | Jhenaidah_132kV | Chuadanga_132kV | 39 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kurigram_132kVtoLalmonirhat_132kV_Line1 | Kurigram_132kV | Lalmonirhat_132kV | 31 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaNorth_132kVtoChandina_132kV_Line1 | CumillaNorth_132kV | Chandina_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
CumillaNorth_132kVtoChandina_132kV_Line2 | CumillaNorth_132kV | Chandina_132kV | 16 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rajendrapur_132kVtoSripur_132kV_Line1 | Rajendrapur_132kV | Sripur_132kV | 20.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Rajendrapur_132kVtoSripur_132kV_Line2 | Rajendrapur_132kV | Sripur_132kV | 20.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Araihazar_132kVtoBhulta_132kV_Line1 | Araihazar_132kV | Bhulta_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Araihazar_132kVtoBhulta_132kV_Line2 | Araihazar_132kV | Bhulta_132kV | 8 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
DynamicSunSolarPP_132kVtoIshwardi_132kV_Line1 | DynamicSunSolarPP_132kV | Ishwardi_132kV | 22 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
DynamicSunSolarPP_132kVtoIshwardi_132kV_Line2 | DynamicSunSolarPP_132kV | Ishwardi_132kV | 22 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kachua_132kVtoLaksham_132kV_Line1 | Kachua_132kV | Laksham_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kachua_132kVtoLaksham_132kV_Line2 | Kachua_132kV | Laksham_132kV | 32 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chowmuhani_132kVtoLakshmipur_132kV_Line1 | Chowmuhani_132kV | Lakshmipur_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Chowmuhani_132kVtoLakshmipur_132kV_Line2 | Chowmuhani_132kV | Lakshmipur_132kV | 27 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sripur_132kVtoKodda_132kV_Line1 | Sripur_132kV | Kodda_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sripur_132kVtoKodda_132kV_Line2 | Sripur_132kV | Kodda_132kV | 9 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kaliganj_132kVtoMaheshpur_132kV_Line1 | Kaliganj_132kV | Maheshpur_132kV | 26 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Kaliganj_132kVtoMaheshpur_132kV_Line2 | Kaliganj_132kV | Maheshpur_132kV | 26 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132
Sathia_132kVtoPabna64MWSolarPP_132kV_Line1 | Sathia_132kV | Pabna64MWSolarPP_132kV | 34.5 | Grosbeak | 0.1101 | 0.2559 | 6.57e-06 | 132